## SSR
1 | Binding wire |  |  | 70 | PHSSR |  |  | 2016-17
2 | Delifting charges |  |  | 41 |  |  | with SSR
3 | Slab up to 150mm |  |  | 389 | bldg.92
4 | Slab above 300mm |  |  | 418 | bldg.89
5 | Centering Charges Footing/BedBlocks |  |  | 750 | bldg.89 | 305 | Bed blocks
6 | Lifting charges (Concrete) |  |  | 134
7 | Mason Ist Class |  |  | 420 | PHSSR-p6
8 | Mason II nd class/Work Inspector |  |  | 375 | PHSSR-p6
9 | Men mazdoor |  |  | 320 | p11
10 | Woman Mazdoor |  |  | 320 | p11
11 | Centering Charges Ring Beam/Cir Col |  |  | 1206 | PHSSR-p46
12 | Centering Charges Doome |  |  | 2670 | PHSSR-p46 | 6302 | Roof slab | domes
13 | Earth work Initial rate (up to 3M) |  |  | 116.48 | R&B.Ch.11/1
14 | Earth work Initial rate(3-6m) |  |  | 149.76 | R&B.Ch.11/2/A
15 | Earth work Initial rate(above-6m) |  |  | 199.68 | R&B.Ch.11/3/A
16 | Sand filling Charges |  |  | 106.9 | R&B.Ch.11/2/A
17 | Water | rural |  | 77 | M 189
18 | dome slabs centering |  |  | 6302 | buildings
19 | Beams |  |  | 3428 | bldg.89
20 | Column/Braces centering charges |  |  | 1099 | PH P-301 |  |  |  | .61 m
20a | Brace centering charges(Circular) |  |  | 1206 | PH p-47 |  |  |  | 5.49
21 | Column/Walls Circular |  |  | 2041 | bldg.89 |  |  | 3 times | 2nd floor | upto 5.49m
22 | Column above 3.66mt |  |  | 2381 | bldg.89 | 16.67% | 341 | 170.4932 | 1870 | 2381
23 | Beams above 3.66m height |  |  | 4572 | bldg.89 |  | 2002 | 1000.96 | 1569 | 4572
24 | Lintels |  |  | 2344 | bldg.89 | 1068 | Pedestrals
25 | Sun shades 0.6m Width |  |  | 410 | bldg.89
26 | Roof slab up to 150mm thick |  |  | 389 | bldg.89 | 761 | above 3.66m | 194.4922 | 178 | 761
27 | Roof slab 150-300mm thick |  |  | 399 | bldg.89 | 781 | above 3.66m | 199.492 | 183 | 781
28 | Roof slab above 300.0mm thick above 3.66m height |  |  | 818 | bldg.89 | 418 | upto 3.66mts height | 208.9916 | 191 | 818
29 | Helical Stair case |  | 1 sqmt | 480 | bldg.89
30 | Concrete Mixer 10 / 7 cft (0.2 / 0.8 cum) capacity |  |  | 338.6 | P-134 CSSR | item 16
31 | Cost of Diesel for Miller |  | per Lts | 57 | C-SSR p-21
32 | Cost of Petrol for Vibrator per Lts |  |  | 69 | C-SSR p-21 |  | above 3.66m
33 | RCC Vertical wall of circular |  |  | 1115 |  | 1359.8 | 1469
34 | Side walls curved surfaces. |  |  | 2463 | PH p-47 |  | 1909.7
35 | Side walls St Surface |  |  | 2192 | PH p-48
36 | Lifting charges (Mortar) |  |  | 67 |  |  |  | 67
37 | Pig Iron as per SSR |  |  | 26000 | PH p-108
38 | Coke as per SSR |  |  | 36570 | PH p-108
39 | CI specials per Kg as per SSR |  |  | 73.7 | PH p-108
40 | Seignorage charges Earth |  |  | 22
| RCC Vertical wall of straight |  |  | 876 | 876 | both faces
41 | wood primer |  |  | 158 | Bld SSR-31-S.No.478
42 | cost of paint |  |  | 276 | Bld SSR-28-S.No382
43 | cost of white cement |  |  | 29 | Bld SSR-88-S.No943
44 | Snowcem @ |  |  | 53 | Bld SSR-27-S.No376 | water proof cement
45 | Rolling Shutters80x1.25mm |  |  | 2861 | Bld SSR-18-S.No156
46 | Painter 1st class |  |  | 480
47 | Acco Proof powder |  |  | 75 | (water proofing compound) as per buildings ssr
48 | weigh Batcher hire charges |  |  | 556.8
|  | RSF | Rate
| 1 | 2 | 4.85 | 53 |  |  | Size | DI D/F Gate valves (soft seated) upto 600mm dia and butter fly valves above 600mm With 5% Extra for Conveyance-PN1.6 | As per SSR 2015-16
| 2 | 5 | 4.01 | 53 |  |  | 80 | 11025 | 10500
| 3 | 10 | 3.53 | 53 |  |  | 100 | 12368 | 11779 |  | interpolation
| 4 | 20 | 3.09 | 53 |  |  | 125 | 15843 | 15089 |  | 14723.75
| 5 | 30 | 2.71 | 53 |  |  | 150 | 19473 | 18546 |  | 15089.375
| 6 | 40 | 2.71 | 53 |  |  | 200 | 28613 | 27250 |  | 15455
|  | Cement | 6400 |  |  |  | 250 | 36488 | 34750
|  | Steel | 42000 |  |  |  | 300 | 67740 | 64514
[7 empty] | 350 | 94238 | 89750
| OHSR | [5 empty] | 400 | 120488 | 114750 |  |  | per MT
| 10000 | 65.56 | PH p-51 |  |  |  | 450 | 197925 | 188500 |  |  |  | Upto 10,000 Litres capacity | 65.56
| 15000 | 45.09 |  |  |  |  | 500 | 253050 | 241000 |  |  |  | 15,000 Litres capacity | 45.09
| 20000 | 44.31 |  |  |  |  | 600 | 358050 | 341000 |  |  |  | 20,000 Litres capacity | 44.31
| 40000 | 39.22 | [10 empty] | 40,000 Litres capacity | 39.22
| 60000 | 29.76 | [10 empty] | 60,000 Litres capacity | 29.76
| 90000 | 28.0425 | [10 empty] | 1,00,000 Litres capacity | 27.47 | 2.29 | 0.5725 | 28.0425 | 90kl
| 120000 | 26.786 | [10 empty] | 2,00,000 Litres capacity | 24.05 | 3.42 | 0.342 | 26.786 | 120kl
| 150000 | 25.97 | [10 empty] | 3,00,000 Litres capacity | 22.57 | 1.48 |  | 25.97 | 150kl
| 200000 | 24.05 | [10 empty] | 4,00,000 Litres capacity | 19.9 |  | 0.74 | 23.31 | 250kl
| 250000 | 23.31 | [10 empty] | 4,50,000 Litres capacity | 17.25
| 300000 | 22.57
| Cement rate | 6400
| Steel Rate | 42000
COMMON SSR 2015-16
SSR-P
107.9 | Loading | 107.9 | 125.2 | 0
| unloading | 38.7 | 62.6 | 212 |  | RR stone | shabad stone
|  | 146.6 | 187.8 | 212 |  |  | 117.7 | 5km | old
| Kms | Sand | Metal | Bricks |  |  | 177.45 | 5-15km
| 0.25 | 177.6 | 217.7 | 261.8 |  | 92.5 | 1380.4 | 15-30Km
| 0.5 | 177.6 | 217.7 | 261.8 |  | 92.5 | 1675.55 | above 30 km
| 1 | 177.6 | 217.7 | 261.8 |  | 92.5 | 83.7775
| 2 | 190 | 229.7 | 281.8 |  | 104.5
For metal | 3 | 204.5 | 245.7 | 305 |  | 120.5
and sand | 4 | 216.9 | 258.1 | 324.9 | For Bricks | 132.9 | shabad stone | For shabad
P 130 | 5 | 229.3 | 270.5 | 344.9 | P 130 | 145.3 | 121.6 |  | 5km
12.4 | 6 | 241.7 | 282.9 | 364.8 | 19.9 | 157.7 | 139.8 | 18.2
| 7 | 254.1 | 295.3 | 384.7 |  | 170.1 | 158
| 8 | 266.5 | 307.7 | 404.6 |  | 182.5 | 176.2
| 9 | 278.9 | 320.1 | 424.5 |  | 194.9 | 194.4
| 10 | 291.3 | 332.5 | 444.4 |  | 207.3 | 212.6
| 11 | 303.7 | 344.9 | 464.3 |  | 219.7 | 230.8
| 12 | 316.1 | 357.3 | 484.2 |  | 232.1 | 249
| 13 | 328.5 | 369.7 | 504.1 |  | 244.5 | 267.2
| 14 | 340.9 | 382.1 | 524 |  | 256.9 | 285.4
| 15 | 353.3 | 394.5 | 543.9 |  | 269.3 | 303.6
| 16 | 365.7 | 406.9 | 563.8 |  | 281.7 | 321.8
| 17 | 378.1 | 419.3 | 583.7 |  | 294.1 | 340
| 18 | 390.5 | 431.7 | 603.6 |  | 306.5 | 358.2
| 19 | 402.9 | 444.1 | 623.5 |  | 318.9 | 376.4
| 20 | 415.3 | 456.5 | 643.4 |  | 331.3 | 394.6
| 21 | 427.7 | 468.9 | 663.3 |  | 343.7 | 412.8
| 22 | 440.1 | 481.3 | 683.2 |  | 356.1 | 431
| 23 | 452.5 | 493.7 | 703.1 |  | 368.5 | 449.2
| 24 | 464.9 | 506.1 | 723 |  | 380.9 | 467.4
| 25 | 477.3 | 518.5 | 742.9 |  | 393.3 | 485.6
| 26 | 489.7 | 530.9 | 762.8 |  | 405.7 | 503.8
| 27 | 502.1 | 543.3 | 782.7 |  | 418.1 | 522
| 28 | 514.5 | 555.7 | 802.6 |  | 430.5 | 540.2
| 29 | 526.9 | 568.1 | 822.5 |  | 442.9 | 558.4
| 30 | 539.3 | 580.5 | 842.4 |  | 455.3 | 576.6
10.3 | 31 | 549.6 | 590.8 | 859 | 16.6 | 465.6 | 591.8 | 15.2
| 32 | 559.9 | 601.1 | 875.6 |  | 475.9 | 607
| 33 | 570.2 | 611.4 | 892.2 |  | 486.2 | 622.2
| 34 | 580.5 | 621.7 | 908.8 |  | 496.5 | 637.4
| 35 | 590.8 | 632 | 925.4 |  | 506.8 | 652.6
| 36 | 601.1 | 642.3 | 942 |  | 517.1 | 667.8
| 37 | 611.4 | 652.6 | 958.6 |  | 527.4 | 683
| 38 | 621.7 | 662.9 | 975.2 |  | 537.7 | 698.2
| 39 | 632 | 673.2 | 991.8 |  | 548 | 713.4
| 40 | 642.3 | 683.5 | 1008.4 |  | 558.3 | 728.6
| 41 | 652.6 | 693.8 | 1025 |  | 568.6 | 743.8
| 42 | 662.9 | 704.1 | 1041.6 |  | 578.9 | 759
| 43 | 673.2 | 714.4 | 1058.2 |  | 589.2 | 774.2
| 44 | 683.5 | 724.7 | 1074.8 |  | 599.5 | 789.4
| 45 | 693.8 | 735 | 1091.4 |  | 609.8 | 804.6
| 46 | 704.1 | 745.3 | 1108 |  | 620.1 | 819.8
| 47 | 714.4 | 755.6 | 1124.6 |  | 630.4 | 835
| 48 | 724.7 | 765.9 | 1141.2 |  | 640.7 | 850.2
| 49 | 735 | 776.2 | 1157.8 |  | 651 | 865.4
| 50 | 745.3 | 786.5 | 1174.4 |  | 661.3 | 880.6
| 51 | 755.6 | 796.8 | 1191 |  | 671.6 | 895.8
| 52 | 765.9 | 807.1 | 1207.6 |  | 681.9 | 911
| 53 | 776.2 | 817.4 | 1224.2 |  | 692.2 | 926.2
| 54 | 786.5 | 827.7 | 1240.8 |  | 702.5 | 941.4
| 55 | 796.8 | 838 | 1257.4 |  | 712.8 | 956.6
| 56 | 807.1 | 848.3 | 1274 |  | 723.1 | 971.8
| 57 | 817.4 | 858.6 | 1290.6 |  | 733.4 | 987
| 58 | 827.7 | 868.9 | 1307.2 |  | 743.7 | 1002.2
| 59 | 838 | 879.2 | 1323.8 |  | 754 | 1017.4
| 60 | 848.3 | 889.5 | 1340.4 |  | 764.3 | 1032.6
| 61 | 858.6 | 899.8 | 1357 |  | 774.6 | 1047.8
| 62 | 868.9 | 910.1 | 1373.6 |  | 784.9 | 1063
| 63 | 879.2 | 920.4 | 1390.2 |  | 795.2 | 1078.2
| 64 | 889.5 | 930.7 | 1406.8 |  | 805.5 | 1093.4
| 65 | 899.8 | 941 | 1423.4 |  | 815.8 | 1108.6
| 66 | 910.1 | 951.3 | 1440 |  | 826.1 | 1123.8
| 67 | 920.4 | 961.6 | 1456.6 |  | 836.4 | 1139
| 68 | 930.7 | 971.9 | 1473.2 |  | 846.7 | 1154.2
| 69 | 941 | 982.2 | 1489.8 |  | 857 | 1169.4
| 70 | 951.3 | 992.5 | 1506.4 |  | 867.3 | 1184.6
| 71 | 961.6 | 1002.8 | 1523 |  | 877.6 | 1199.8
| 72 | 971.9 | 1013.1 | 1539.6 |  | 887.9 | 1215
| 73 | 982.2 | 1023.4 | 1556.2 |  | 898.2 | 1230.2
| 74 | 992.5 | 1033.7 | 1572.8 |  | 908.5 | 1245.4
| 75 | 1002.8 | 1044 | 1589.4 |  | 918.8 | 1260.6
| 76 | 1013.1 | 1054.3 | 1606 |  | 929.1 | 1275.8
| 77 | 1023.4 | 1064.6 | 1622.6 |  | 939.4 | 1291
| 78 | 1033.7 | 1074.9 | 1639.2 |  | 949.7 | 1306.2
| 79 | 1044 | 1085.2 | 1655.8 |  | 960 | 1321.4
| 80 | 1054.3 | 1095.5 | 1672.4 |  | 970.3 | 1336.6
| 81 | 1064.6 | 1105.8 | 1689 |  | 980.6 | 1351.8
| 82 | 1074.9 | 1116.1 | 1705.6 |  | 990.9 | 1367
| 83 | 1085.2 | 1126.4 | 1722.2 |  | 1001.2 | 1382.2
| 84 | 1095.5 | 1136.7 | 1738.8 |  | 1011.5 | 1397.4
| 85 | 1105.8 | 1147 | 1755.4 |  | 1021.8 | 1412.6
| 86 | 1116.1 | 1157.3 | 1772 |  | 1032.1 | 1427.8
| 87 | 1126.4 | 1167.6 | 1788.6 |  | 1042.4 | 1443
| 88 | 1136.7 | 1177.9 | 1805.2 |  | 1052.7 | 1458.2
| 89 | 1147 | 1188.2 | 1821.8 |  | 1063 | 1473.4
| 90 | 1157.3 | 1198.5 | 1838.4 |  | 1073.3 | 1488.6
| 91 | 1167.6 | 1208.8 | 1855 |  | 1083.6 | 1503.8
| 92 | 1177.9 | 1219.1 | 1871.6 |  | 1093.9 | 1519
| 93 | 1188.2 | 1229.4 | 1888.2 |  | 1104.2 | 1534.2
| 94 | 1198.5 | 1239.7 | 1904.8 |  | 1114.5 | 1549.4
| 95 | 1208.8 | 1250 | 1921.4 |  | 1124.8 | 1564.6
| 96 | 1219.1 | 1260.3 | 1938 |  | 1135.1 | 1579.8
| 97 | 1229.4 | 1270.6 | 1954.6 |  | 1145.4 | 1595
| 98 | 1239.7 | 1280.9 | 1971.2 |  | 1155.7 | 1610.2
| 99 | 1250 | 1291.2 | 1987.8 |  | 1166 | 1625.4
| 100 | 1260.3 | 1301.5 | 2004.4 |  | 1176.3 | 1640.6
| 101 | 1270.6 | 1311.8 | 2021 |  | 1186.6 | 1655.8
| 102 | 1280.9 | 1322.1 | 2037.6 |  | 1196.9 | 1671
| 103 | 1291.2 | 1332.4 | 2054.2 |  | 1207.2 | 1686.2
| 104 | 1301.5 | 1342.7 | 2070.8 |  | 1217.5 | 1701.4
| 105 | 1311.8 | 1353 | 2087.4 |  | 1227.8 | 1716.6
| 106 | 1322.1 | 1363.3 | 2104 |  | 1238.1 | 1731.8
| 107 | 1332.4 | 1373.6 | 2120.6 |  | 1248.4 | 1747
| 108 | 1342.7 | 1383.9 | 2137.2 |  | 1258.7 | 1762.2
| 109 | 1353 | 1394.2 | 2153.8 |  | 1269 | 1777.4
| 110 | 1363.3 | 1404.5 | 2170.4 |  | 1279.3 | 1792.6
| 111 | 1373.6 | 1414.8 | 2187 |  | 1289.6 | 1807.8
| 112 | 1383.9 | 1425.1 | 2203.6 |  | 1299.9 | 1823
| 113 | 1394.2 | 1435.4 | 2220.2 |  | 1310.2 | 1838.2
| 114 | 1404.5 | 1445.7 | 2236.8 |  | 1320.5 | 1853.4
| 115 | 1414.8 | 1456 | 2253.4 |  | 1330.8 | 1868.6
| 116 | 1425.1 | 1466.3 | 2270 |  | 1341.1 | 1883.8
| 117 | 1435.4 | 1476.6 | 2286.6 |  | 1351.4 | 1899
| 118 | 1445.7 | 1486.9 | 2303.2 |  | 1361.7 | 1914.2
| 119 | 1456 | 1497.2 | 2319.8 |  | 1372 | 1929.4
| 120 | 1466.3 | 1507.5 | 2336.4 |  | 1382.3 | 1944.6
| 121 | 1476.6 | 1517.8 | 2353 |  | 1392.6 | 1959.8
| 122 | 1486.9 | 1528.1 | 2369.6 |  | 1402.9 | 1975
| 123 | 1497.2 | 1538.4 | 2386.2 |  | 1413.2 | 1990.2
| 124 | 1507.5 | 1548.7 | 2402.8 |  | 1423.5 | 2005.4
| 125 | 1517.8 | 1559 | 2419.4 |  | 1433.8 | 2020.6
| 126 | 1528.1 | 1569.3 | 2436 |  | 1444.1 | 2035.8
| 127 | 1538.4 | 1579.6 | 2452.6 |  | 1454.4 | 2051
| 128 | 1548.7 | 1589.9 | 2469.2 |  | 1464.7 | 2066.2
| 129 | 1559 | 1600.2 | 2485.8 |  | 1475 | 2081.4
| 130 | 1569.3 | 1610.5 | 2502.4 |  | 1485.3 | 2096.6
| 131 | 1579.6 | 1620.8 | 2519 |  | 1495.6 | 2111.8
| 132 | 1589.9 | 1631.1 | 2535.6 |  | 1505.9 | 2127
| 133 | 1600.2 | 1641.4 | 2552.2 |  | 1516.2 | 2142.2
| 134 | 1610.5 | 1651.7 | 2568.8 |  | 1526.5 | 2157.4
| 135 | 1620.8 | 1662 | 2585.4 |  | 1536.8 | 2172.6
| 136 | 1631.1 | 1672.3 | 2602 |  | 1547.1 | 2187.8
| 137 | 1641.4 | 1682.6 | 2618.6 |  | 1557.4 | 2203
| 138 | 1651.7 | 1692.9 | 2635.2 |  | 1567.7 | 2218.2
| 139 | 1662 | 1703.2 | 2651.8 |  | 1578 | 2233.4
| 140 | 1672.3 | 1713.5 | 2668.4 |  | 1588.3 | 2248.6
| 141 | 1682.6 | 1723.8 | 2685 |  | 1598.6 | 2263.8
| 142 | 1692.9 | 1734.1 | 2701.6 |  | 1608.9 | 2279
| 143 | 1703.2 | 1744.4 | 2718.2 |  | 1619.2 | 2294.2
| 144 | 1713.5 | 1754.7 | 2734.8 |  | 1629.5 | 2309.4
| 145 | 1723.8 | 1765 | 2751.4 |  | 1639.8 | 2324.6
| 146 | 1734.1 | 1775.3 | 2768 |  | 1650.1 | 2339.8
| 147 | 1744.4 | 1785.6 | 2784.6 |  | 1660.4 | 2355
| 148 | 1754.7 | 1795.9 | 2801.2 |  | 1670.7 | 2370.2
| 149 | 1765 | 1806.2 | 2817.8 |  | 1681 | 2385.4
| 150 | 1775.3 | 1816.5 | 2834.4 |  | 1691.3 | 2400.6
| 151 | 1785.6 | 1826.8 | 2851 |  | 1701.6 | 2415.8
| 152 | 1795.9 | 1837.1 | 2867.6 |  | 1711.9 | 2431
| 153 | 1806.2 | 1847.4 | 2884.2 |  | 1722.2 | 2446.2
| 154 | 1816.5 | 1857.7 | 2900.8 |  | 1732.5 | 2461.4
| 155 | 1826.8 | 1868 | 2917.4 |  | 1742.8 | 2476.6
| 156 | 1837.1 | 1878.3 | 2934 |  | 1753.1 | 2491.8
| 157 | 1847.4 | 1888.6 | 2950.6 |  | 1763.4 | 2507
| 158 | 1857.7 | 1898.9 | 2967.2 |  | 1773.7 | 2522.2
| 159 | 1868 | 1909.2 | 2983.8 |  | 1784 | 2537.4
| 160 | 1878.3 | 1919.5 | 3000.4 |  | 1794.3 | 2552.6
| 161 | 1888.6 | 1929.8 | 3017 |  | 1804.6 | 2567.8
| 162 | 1898.9 | 1940.1 | 3033.6 |  | 1814.9 | 2583
| 163 | 1909.2 | 1950.4 | 3050.2 |  | 1825.2 | 2598.2
| 164 | 1919.5 | 1960.7 | 3066.8 |  | 1835.5 | 2613.4
| 165 | 1929.8 | 1971 | 3083.4 |  | 1845.8 | 2628.6
| 166 | 1940.1 | 1981.3 | 3100 |  | 1856.1 | 2643.8
| 167 | 1950.4 | 1991.6 | 3116.6 |  | 1866.4 | 2659
| 168 | 1960.7 | 2001.9 | 3133.2 |  | 1876.7 | 2674.2
| 169 | 1971 | 2012.2 | 3149.8 |  | 1887 | 2689.4
| 170 | 1981.3 | 2022.5 | 3166.4 |  | 1897.3 | 2704.6
| 171 | 1991.6 | 2032.8 | 3183 |  | 1907.6 | 2719.8
| 172 | 2001.9 | 2043.1 | 3199.6 |  | 1917.9 | 2735
| 173 | 2012.2 | 2053.4 | 3216.2 |  | 1928.2 | 2750.2
| 174 | 2022.5 | 2063.7 | 3232.8 |  | 1938.5 | 2765.4
| 175 | 2032.8 | 2074 | 3249.4 |  | 1948.8 | 2780.6
| 176 | 2043.1 | 2084.3 | 3266 |  | 1959.1 | 2795.8
| 177 | 2053.4 | 2094.6 | 3282.6 |  | 1969.4 | 2811
| 178 | 2063.7 | 2104.9 | 3299.2 |  | 1979.7 | 2826.2
| 179 | 2074 | 2115.2 | 3315.8 |  | 1990 | 2841.4
| 180 | 2084.3 | 2125.5 | 3332.4 |  | 2000.3 | 2856.6
| 181 | 2094.6 | 2135.8 | 3349 |  | 2010.6 | 2871.8
| 182 | 2104.9 | 2146.1 | 3365.6 |  | 2020.9 | 2887
| 183 | 2115.2 | 2156.4 | 3382.2 |  | 2031.2 | 2902.2
| 184 | 2125.5 | 2166.7 | 3398.8 |  | 2041.5 | 2917.4
| 185 | 2135.8 | 2177 | 3415.4 |  | 2051.8 | 2932.6
| 186 | 2146.1 | 2187.3 | 3432 |  | 2062.1 | 2947.8
| 187 | 2156.4 | 2197.6 | 3448.6 |  | 2072.4 | 2963
| 188 | 2166.7 | 2207.9 | 3465.2 |  | 2082.7 | 2978.2
| 189 | 2177 | 2218.2 | 3481.8 |  | 2093 | 2993.4
| 190 | 2187.3 | 2228.5 | 3498.4 |  | 2103.3 | 3008.6
| 191 | 2197.6 | 2238.8 | 3515 |  | 2113.6 | 3023.8
| 192 | 2207.9 | 2249.1 | 3531.6 |  | 2123.9 | 3039
| 193 | 2218.2 | 2259.4 | 3548.2 |  | 2134.2 | 3054.2
| 194 | 2228.5 | 2269.7 | 3564.8 |  | 2144.5 | 3069.4
| 195 | 2238.8 | 2280 | 3581.4 |  | 2154.8 | 3084.6
| 196 | 2249.1 | 2290.3 | 3598 |  | 2165.1 | 3099.8
| 197 | 2259.4 | 2300.6 | 3614.6 |  | 2175.4 | 3115
| 198 | 2269.7 | 2310.9 | 3631.2 |  | 2185.7 | 3130.2
| 199 | 2280 | 2321.2 | 3647.8 |  | 2196 | 3145.4
| 200 | 2290.3 | 2331.5 | 3664.4 |  | 2206.3 | 3160.6
| 201 | 2300.6 | 2341.8 | 3681 |  | 2216.6 | 3175.8
| 202 | 2310.9 | 2352.1 | 3697.6 |  | 2226.9 | 3191
| 203 | 2321.2 | 2362.4 | 3714.2 |  | 2237.2 | 3206.2
| 204 | 2331.5 | 2372.7 | 3730.8 |  | 2247.5 | 3221.4
| 205 | 2341.8 | 2383 | 3747.4 |  | 2257.8 | 3236.6
| 206 | 2352.1 | 2393.3 | 3764 |  | 2268.1 | 3251.8
| 207 | 2362.4 | 2403.6 | 3780.6 |  | 2278.4 | 3267
| 208 | 2372.7 | 2413.9 | 3797.2 |  | 2288.7 | 3282.2
| 209 | 2383 | 2424.2 | 3813.8 |  | 2299 | 3297.4
| 210 | 2393.3 | 2434.5 | 3830.4 |  | 2309.3 | 3312.6
| 211 | 2403.6 | 2444.8 | 3847 |  | 2319.6 | 3327.8
| 212 | 2413.9 | 2455.1 | 3863.6 |  | 2329.9 | 3343
| 213 | 2424.2 | 2465.4 | 3880.2 |  | 2340.2 | 3358.2
| 214 | 2434.5 | 2475.7 | 3896.8 |  | 2350.5 | 3373.4
| 215 | 2444.8 | 2486 | 3913.4 |  | 2360.8 | 3388.6
| 216 | 2455.1 | 2496.3 | 3930 |  | 2371.1 | 3403.8
| 217 | 2465.4 | 2506.6 | 3946.6 |  | 2381.4 | 3419
| 218 | 2475.7 | 2516.9 | 3963.2 |  | 2391.7 | 3434.2
| 219 | 2486 | 2527.2 | 3979.8 |  | 2402 | 3449.4
| 220 | 2496.3 | 2537.5 | 3996.4 |  | 2412.3 | 3464.6
| 221 | 2506.6 | 2547.8 | 4013 |  | 2422.6 | 3479.8
| 222 | 2516.9 | 2558.1 | 4029.6 |  | 2432.9 | 3495
| 223 | 2527.2 | 2568.4 | 4046.2 |  | 2443.2 | 3510.2
| 224 | 2537.5 | 2578.7 | 4062.8 |  | 2453.5 | 3525.4
| 225 | 2547.8 | 2589 | 4079.4 |  | 2463.8 | 3540.6
| 226 | 2558.1 | 2599.3 | 4096 |  | 2474.1 | 3555.8
| 227 | 2568.4 | 2609.6 | 4112.6 |  | 2484.4 | 3571
| 228 | 2578.7 | 2619.9 | 4129.2 |  | 2494.7 | 3586.2
| 229 | 2589 | 2630.2 | 4145.8 |  | 2505 | 3601.4
| 230 | 2599.3 | 2640.5 | 4162.4 |  | 2515.3 | 3616.6
| 231 | 2609.6 | 2650.8 | 4179 |  | 2525.6 | 3631.8
| 232 | 2619.9 | 2661.1 | 4195.6 |  | 2535.9 | 3647

## CI specials
|  | with SSR | 2016-17
|  | Rate per Kg as per SSR |  |  | 73.7
| Pig iron-SSR |  | 26000
| Coke-SSR |  | 36570
| Prsent Pig iron Cost |  | 26000
| Present Coke Cost |  | 36570
Weight of Double Flanged CI pipes as per 7181 : 1986 (Table 2)
0.6 mtrs Length | [9 empty] | tail piece
Sno. | Dia | Wt. of 1m length | wt. of 0.6 m length | Wt. of one flange | wt. of double flange | Total wt. | rate per Kg | Amount | Revised cost | wt | rate | Revised cost
mm
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | 80 | 19.8 | 11.88 | 3.7 | 7.4 | 19.28 | 73.7 | 1420.936 | 1420.936 | 15.58 | 1148.25 | 1148.25
2 | 100 | 25.4 | 15.24 | 4.2 | 8.4 | 23.64 | 73.7 | 1742.268 | 1742.268 | 19.44 | 1432.73 | 1432.73
3 | 125 | 33.1 | 19.86 | 5.3 | 10.6 | 30.46 | 73.7 | 2244.902 | 2244.902 | 25.16 | 1854.29 | 1854.29
4 | 150 | 41.6 | 24.96 | 6.7 | 13.4 | 38.36 | 73.7 | 2827.132 | 2827.132 | 31.66 | 2333.34 | 2333.34
5 | 200 | 60.1 | 36.06 | 9.3 | 18.6 | 54.66 | 73.7 | 4028.442 | 4028.442 | 45.36 | 3343.03 | 3343.03
6 | 250 | 81.8 | 49.08 | 12 | 24 | 73.08 | 73.7 | 5385.996 | 5385.996 | 61.08 | 4501.6 | 4501.6
7 | 300 | 106.1 | 63.66 | 14.8 | 29.6 | 93.26 | 73.7 | 6873.262 | 6873.262 | 78.46 | 5782.5 | 5782.5
8 | 350 | 133.5 | 80.1 | 19 | 38 | 118.1 | 73.7 | 8703.97 | 8703.97 | 99.1 | 7303.67 | 7303.67
9 | 400 | 162.6 | 97.56 | 23.4 | 46.8 | 144.36 | 73.7 | 10639.332 | 10639.332 | 120.96 | 8914.75 | 8914.75
10 | 450 | 197 | 118.2 | 26.5 | 53 | 171.2 | 73.7 | 12617.44 | 12617.44 | 144.7 | 10664.39 | 10664.39
11 | 500 | 229.3 | 137.58 | 32.1 | 64.2 | 201.78 | 73.7 | 14871.186 | 14871.186 | 169.68 | 12505.42 | 12505.42
12 | 600 | 306.5 | 183.9 | 44 | 88 | 271.9 | 73.7 | 20039.03 | 20039.03 | 227.9 | 16796.23 | 16796.23
0.9 mtrs Length | [9 empty] | tail piece
Sno. | Dia | Wt. of 1m length | wt. of 0.9 m length | Wt. of one flange | wt. of double flange | Total wt. | rate per Kg | Amount | Revised cost | wt | rate | Revised cost
mm
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | 80 | 19.8 | 17.82 | 3.7 | 7.4 | 25.22 | 73.7 | 1858.714 | 1858.714 | 21.52 | 1586.02 | 1586.02
2 | 100 | 25.4 | 22.86 | 4.2 | 8.4 | 31.26 | 73.7 | 2303.862 | 2303.862 | 27.06 | 1994.32 | 1994.32
3 | 125 | 33.1 | 29.79 | 5.3 | 10.6 | 40.39 | 73.7 | 2976.743 | 2976.743 | 35.09 | 2586.13 | 2586.13
4 | 150 | 41.6 | 37.44 | 6.7 | 13.4 | 50.84 | 73.7 | 3746.908 | 3746.908 | 44.14 | 3253.12 | 3253.12
5 | 200 | 60.1 | 54.09 | 9.3 | 18.6 | 72.69 | 73.7 | 5357.253 | 5357.253 | 63.39 | 4671.84 | 4671.84
6 | 250 | 81.8 | 73.62 | 12 | 24 | 97.62 | 73.7 | 7194.594 | 7194.594 | 85.62 | 6310.19 | 6310.19
7 | 300 | 106.1 | 95.49 | 14.8 | 29.6 | 125.09 | 73.7 | 9219.133 | 9219.133 | 110.29 | 8128.37 | 8128.37
8 | 350 | 133.5 | 120.15 | 19 | 38 | 158.15 | 73.7 | 11655.655 | 11655.655 | 139.15 | 10255.36 | 10255.36
9 | 400 | 162.6 | 146.34 | 23.4 | 46.8 | 193.14 | 73.7 | 14234.418 | 14234.418 | 169.74 | 12509.84 | 12509.84
10 | 450 | 197 | 177.3 | 26.5 | 53 | 230.3 | 73.7 | 16973.11 | 16973.11 | 203.8 | 15020.06 | 15020.06
11 | 500 | 229.3 | 206.37 | 32.1 | 64.2 | 270.57 | 73.7 | 19941.009 | 19941.009 | 238.47 | 17575.24 | 17575.24
12 | 600 | 306.5 | 275.85 | 44 | 88 | 363.85 | 73.7 | 26815.745 | 26815.745 | 319.85 | 23572.95 | 23572.95
1.0 mtrs Length | [9 empty] | tail piece
Sno. | Dia | Wt. of 1m length | wt. of 1.0 m length | Wt. of one flange | wt. of double flange | Total wt. | rate per Kg | Amount | Revised cost | wt | rate | Revised cost
mm
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | 80 | 19.8 | 19.8 | 3.7 | 7.4 | 27.2 | 73.7 | 2004.64 | 2004.64 | 23.5 | 1731.95 | 1731.95
2 | 100 | 25.4 | 25.4 | 4.2 | 8.4 | 33.8 | 73.7 | 2491.06 | 2491.06 | 29.6 | 2181.52 | 2181.52
3 | 125 | 33.1 | 33.1 | 5.3 | 10.6 | 43.7 | 73.7 | 3220.69 | 3220.69 | 38.4 | 2830.08 | 2830.08
4 | 150 | 41.6 | 41.6 | 6.7 | 13.4 | 55 | 73.7 | 4053.5 | 4053.5 | 48.3 | 3559.71 | 3559.71
5 | 200 | 60.1 | 60.1 | 9.3 | 18.6 | 78.7 | 73.7 | 5800.19 | 5800.19 | 69.4 | 5114.78 | 5114.78
6 | 250 | 81.8 | 81.8 | 12 | 24 | 105.8 | 73.7 | 7797.46 | 7797.46 | 93.8 | 6913.06 | 6913.06
7 | 300 | 106.1 | 106.1 | 14.8 | 29.6 | 135.7 | 73.7 | 10001.09 | 10001.09 | 120.9 | 8910.33 | 8910.33
8 | 350 | 133.5 | 133.5 | 19 | 38 | 171.5 | 73.7 | 12639.55 | 12639.55 | 152.5 | 11239.25 | 11239.25
9 | 400 | 162.6 | 162.6 | 23.4 | 46.8 | 209.4 | 73.7 | 15432.78 | 15432.78 | 186 | 13708.2 | 13708.2
10 | 450 | 197 | 197 | 26.5 | 53 | 250 | 73.7 | 18425 | 18425 | 223.5 | 16471.95 | 16471.95
11 | 500 | 229.3 | 229.3 | 32.1 | 64.2 | 293.5 | 73.7 | 21630.95 | 21630.95 | 261.4 | 19265.18 | 19265.18
12 | 600 | 306.5 | 306.5 | 44 | 88 | 394.5 | 73.7 | 29074.65 | 29074.65 | 350.5 | 25831.85 | 25831.85
2.0 mtrs Length
Sno. | Dia | Wt. of 1m length | wt. of 2.0 m length | Wt. of one flange | wt. of double flange | Total wt. | rate per Kg | Amount | Revised cost
mm
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | 80 | 19.8 | 39.6 | 3.7 | 7.4 | 47 | 73.7 | 3463.9 | 3463.9
2 | 100 | 25.4 | 50.8 | 4.2 | 8.4 | 59.2 | 73.7 | 4363.04 | 4363.04
3 | 125 | 33.1 | 66.2 | 5.3 | 10.6 | 76.8 | 73.7 | 5660.16 | 5660.16
4 | 150 | 41.6 | 83.2 | 6.7 | 13.4 | 96.6 | 73.7 | 7119.42 | 7119.42
5 | 200 | 60.1 | 120.2 | 9.3 | 18.6 | 138.8 | 73.7 | 10229.56 | 10229.56
6 | 250 | 81.8 | 163.6 | 12 | 24 | 187.6 | 73.7 | 13826.12 | 13826.12
7 | 300 | 106.1 | 212.2 | 14.8 | 29.6 | 241.8 | 73.7 | 17820.66 | 17820.66
8 | 350 | 133.5 | 267 | 19 | 38 | 305 | 73.7 | 22478.5 | 22478.5
9 | 400 | 162.6 | 325.2 | 23.4 | 46.8 | 372 | 73.7 | 27416.4 | 27416.4
10 | 450 | 197 | 394 | 26.5 | 53 | 447 | 73.7 | 32943.9 | 32943.9
11 | 500 | 229.3 | 458.6 | 32.1 | 64.2 | 522.8 | 73.7 | 38530.36 | 38530.36
12 | 600 | 306.5 | 613 | 44 | 88 | 701 | 73.7 | 51663.7 | 51663.7
2.75 mtrs Length
Sno. | Dia | Wt. of 1m length | wt. of 2.75 m length | Wt. of one flange | wt. of double flange | Total wt. | rate per Kg | Amount | Revised cost
mm
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | 80 | 19.8 | 54.45 | 3.7 | 7.4 | 61.85 | 73.7 | 4558.345 | 4558.345
2 | 100 | 25.4 | 69.85 | 4.2 | 8.4 | 78.25 | 73.7 | 5767.025 | 5767.025
3 | 125 | 33.1 | 91.025 | 5.3 | 10.6 | 101.625 | 73.7 | 7489.7625 | 7489.7625
4 | 150 | 41.6 | 114.4 | 6.7 | 13.4 | 127.8 | 73.7 | 9418.86 | 9418.86
5 | 200 | 60.1 | 165.275 | 9.3 | 18.6 | 183.875 | 73.7 | 13551.5875 | 13551.5875
6 | 250 | 81.8 | 224.95 | 12 | 24 | 248.95 | 73.7 | 18347.615 | 18347.615
7 | 300 | 106.1 | 291.775 | 14.8 | 29.6 | 321.375 | 73.7 | 23685.3375 | 23685.3375
8 | 350 | 133.5 | 367.125 | 19 | 38 | 405.125 | 73.7 | 29857.7125 | 29857.7125
9 | 400 | 162.6 | 447.15 | 23.4 | 46.8 | 493.95 | 73.7 | 36404.115 | 36404.115
10 | 450 | 197 | 541.75 | 26.5 | 53 | 594.75 | 73.7 | 43833.075 | 43833.075
11 | 500 | 229.3 | 630.575 | 32.1 | 64.2 | 694.775 | 73.7 | 51204.9175 | 51204.9175
12 | 600 | 306.5 | 842.875 | 44 | 88 | 930.875 | 73.7 | 68605.4875 | 68605.4875
Rates of various materials-With Price Variation
| Size | 2m d/f | .9 d/f | .6 d/f | bellmouth | 90 bend | tpiece | DuFbend | semicir | DI D/F Gate valves With 5% Extra for Conveyance-PN1.6
| 80 | 3463.9 | 1858.714 | 1420.936 | 515.9 | 958.1 | 1148.25 | 1547.7 | 1842.5 | 11025
| 100 | 4363.04 | 2303.862 | 1742.268 | 663.3 | 1252.9 | 1432.73 | 1916.2 | 2579.5 | 12368
| 125 | 5660.16 | 2976.743 | 2244.902 | 884.4 | 1695.1 | 1854.29 | 2653.2 | 3316.5 | 15843
| 150 | 7119.42 | 3746.908 | 2827.132 | 1105.5 | 2284.7 | 2333.34 | 3463.9 | 4790.5 | 19473
| 200 | 10229.56 | 5357.253 | 4028.442 | 1695.1 | 3611.3 | 3343.03 | 5453.8 | 7370 | 28613
| 250 | 13826.12 | 7194.594 | 5385.996 | 2284.7 | 5306.4 | 4501.6 | 8180.7 | 11792 | 36488
| 300 | 17820.66 | 9219.133 | 6873.262 | 3316.5 | 7370 | 5782.5 | 11497.2 | 15477 | 67740
| 350 | 22478.5 | 11655.655 | 8703.97 | 4274.6 | 10096.9 | 7303.67 | 15771.8 | 25058 | 94238
| 400 | 27416.4 | 14234.418 | 10639.332 | 5896 | 13339.7 | 8914.75 | 20709.7 | 20267.5 | 120488
| 450 | 32943.9 | 16973.11 | 12617.44 | 6854.1 | 16656.2 | 10664.39 | 25795 |  | 197925
| 500 | 38530.36 | 19941.009 | 14871.186 | 8844 | 21373 | 12505.42 | 32870.2 |  | 253050
| 600 | 51663.7 | 26815.745 | 20039.03 | 14813.7 | 32575.4 | 16796.23 | 49157.9 |  | 358050
Weight of Double Flanged CI Bends as per IS : 1538 : 1993 (Table 21& 23)
Double Flanged 90 deg Bends
| Sno. | Dia | Wt. in |  | rate per Kg | Amount | Revised cost
|  | mm | Kg/ Pc
| 1 | 2 | 3 |  | 8 | 9 | 10
| 1 | 80 | 13 |  | 73.7 | 958.1 | 958.1
| 2 | 100 | 17 |  | 73.7 | 1252.9 | 1252.9
| 3 | 125 | 23 |  | 73.7 | 1695.1 | 1695.1
| 4 | 150 | 31 |  | 73.7 | 2284.7 | 2284.7
| 5 | 200 | 49 |  | 73.7 | 3611.3 | 3611.3
| 6 | 250 | 72 |  | 73.7 | 5306.4 | 5306.4
| 7 | 300 | 100 |  | 73.7 | 7370 | 7370
| 8 | 350 | 137 |  | 73.7 | 10096.9 | 10096.9
| 9 | 400 | 181 |  | 73.7 | 13339.7 | 13339.7
| 10 | 450 | 226 |  | 73.7 | 16656.2 | 16656.2
| 11 | 500 | 290 |  | 73.7 | 21373 | 21373
| 12 | 600 | 442 |  | 73.7 | 32575.4 | 32575.4
Double Flanged 45 deg Bends
| Sno. | Dia | Wt. in |  | rate per Kg | Amount | Revised cost
|  | mm | Kg/ Pc
| 1 | 2 | 3 |  | 8 | 9 | 10
| 1 | 80 | 14 |  | 73.7 | 1031.8 | 1031.8
| 2 | 100 | 18 |  | 73.7 | 1326.6 | 1326.6
| 3 | 125 | 25 |  | 73.7 | 1842.5 | 1842.5
| 4 | 150 | 34 |  | 73.7 | 2505.8 | 2505.8
| 5 | 200 | 54 |  | 73.7 | 3979.8 | 3979.8
| 6 | 250 | 80 |  | 73.7 | 5896 | 5896
| 7 | 300 | 112 |  | 73.7 | 8254.4 | 8254.4
| 8 | 350 | 115 |  | 73.7 | 8475.5 | 8475.5
| 9 | 400 | 149 |  | 73.7 | 10981.3 | 10981.3
| 10 | 450 | 185 |  | 73.7 | 13634.5 | 13634.5
| 11 | 500 | 231 |  | 73.7 | 17024.7 | 17024.7
| 12 | 600 | 342 |  | 73.7 | 25205.4 | 25205.4
Weight of Duck Foot Bends as per IS : 1538 : 1993 (Table 22)
Duck Foot Bend
| Sno. | Dia | Wt. in |  | rate per Kg | Amount | Revised cost
|  | mm | Kg/ Pc
| 1 | 2 | 3 |  | 8 | 9 | 10
| 1 | 80 | 21 |  | 73.7 | 1547.7 | 1547.7
| 2 | 100 | 26 |  | 73.7 | 1916.2 | 1916.2
| 3 | 125 | 36 |  | 73.7 | 2653.2 | 2653.2
| 4 | 150 | 47 |  | 73.7 | 3463.9 | 3463.9
| 5 | 200 | 74 |  | 73.7 | 5453.8 | 5453.8
| 6 | 250 | 111 |  | 73.7 | 8180.7 | 8180.7
| 7 | 300 | 156 |  | 73.7 | 11497.2 | 11497.2
| 8 | 350 | 214 |  | 73.7 | 15771.8 | 15771.8
| 9 | 400 | 281 |  | 73.7 | 20709.7 | 20709.7
| 10 | 450 | 350 |  | 73.7 | 25795 | 25795
| 11 | 500 | 446 |  | 73.7 | 32870.2 | 32870.2
| 12 | 600 | 667 |  | 73.7 | 49157.9 | 49157.9
Weight of Bell Mouth Pieces as per IS : 1538 : 1993 (Table 20)
Bell Mouth
| Sno. | Dia | Wt. of bell mouth in |  | rate per Kg | Amount | Revised cost
|  | mm | Kg/ Pc
| 1 | 2 | 3 |  | 8 | 9 | 10
| 1 | 80 | 7 |  | 73.7 | 515.9 | 515.9
| 2 | 100 | 9 |  | 73.7 | 663.3 | 663.3
| 3 | 125 | 12 |  | 73.7 | 884.4 | 884.4
| 4 | 150 | 15 |  | 73.7 | 1105.5 | 1105.5
| 5 | 200 | 23 |  | 73.7 | 1695.1 | 1695.1
| 6 | 250 | 31 |  | 73.7 | 2284.7 | 2284.7
| 7 | 300 | 45 |  | 73.7 | 3316.5 | 3316.5
| 8 | 350 | 58 |  | 73.7 | 4274.6 | 4274.6
| 9 | 400 | 80 |  | 73.7 | 5896 | 5896
| 10 | 450 | 93 |  | 73.7 | 6854.1 | 6854.1
| 11 | 500 | 120 |  | 73.7 | 8844 | 8844
| 12 | 600 | 201 |  | 73.7 | 14813.7 | 14813.7
Semi Circular Bends
| Sno. | Dia | Wt. in |  | rate per Kg | Amount | Revised cost
|  | mm | Kg/ Pc
| 1 | 2 | 3 |  | 8 | 9 | 10
| 1 | 80 | 25 |  | 73.7 | 1842.5 | 1842.5
| 2 | 100 | 35 |  | 73.7 | 2579.5 | 2579.5
| 3 | 125 | 45 |  | 73.7 | 3316.5 | 3316.5
| 4 | 150 | 65 |  | 73.7 | 4790.5 | 4790.5
| 5 | 200 | 100 |  | 73.7 | 7370 | 7370
| 6 | 250 | 160 |  | 73.7 | 11792 | 11792
| 7 | 300 | 210 |  | 73.7 | 15477 | 15477
| 8 | 350 | 340 |  | 73.7 | 25058 | 25058
| 9 | 400 | 275 |  | 73.7 | 20267.5 | 20267.5
| 10 | 500 |  |  |  |  | 0
| 10 | 600 |  |  |  |  | 0

## RAM
| with SSR | 2016-17
Designs
Base year population |  |  | 2015 | 20416
Prospective population (10 years) |  |  | 2027 | 23006
Ultimate population (20 years) |  |  | 2037 | 25413
RSF |  |  |  | 2.43
Sump Dome Type
| Sump well dome type |  |  |  |  | Total depth | 4.2 | 3 |  | Dia
| Side wall thickness |  |  | 0.2 |  | 2st mattu | 1.2 | 1.2 |  | 250
| Ring beam depth |  |  | 0.3 |  | 3 rd mattu | 0 | 0 | 2mts | 1 | 13826
| ring beam breadth |  |  | 0.3 |  | 4 th mattu | 0 | 0 | 0.90 Mts | 2 | 14389
| Dome thickness |  |  | 0.1 |  |  |  |  | 0.60 Mts | 2 | 10772
[9 empty] | Bell Mouth | 1 | 2285
[9 empty] | Duck foot bend | 1 | 8181
[10 empty] | Sum | 49453
Sump well Flat type
| Side wall thickness |  |  | 0.1 |  | Total depth | 3.1 | 3 |  | Dia
| Top Slab thickness |  |  | 0.15 |  | 2st mattu | 0.1 | 0.1 |  | 150
[6 empty] | 3 rd mattu | 0 | 0 | 2mts | 1 | 7119
[6 empty] | 4 th mattu | 0 | 0 | 0.90 Mts | 1 | 3747
[9 empty] | 0.60 Mts | 2 | 5654
[9 empty] | Bell Mouth | 1 | 1106
[9 empty] | Duck foot bend | 1 | 3464
[10 empty] | Sum | 21090
GLBR dome type
| Side wall thickness |  |  | 0.1 |  | Total depth | 1.5 | 1.5
| Ring beam depth |  |  | 0.15 |  | 2st mattu | 0 | 0
| ring beam breadth |  |  | 0.15 |  | 3 rd mattu | 0 | 0
| Dome thickness |  |  | 0.1 |  | 4 th mattu | 0 | 0
GLBR Flat type
| Side wall thickness |  |  | 0.1 |  | Total depth | 1.35 | 1.35
| Top Slab thickness |  |  | 0.15 |  | 2st mattu | 0 | 0
[6 empty] | 3 rd mattu | 0 | 0
[6 empty] | 4 th mattu | 0 | 0
RSF
|  | 5 |  |  | RSF Rates |  |  | 20% | RSF rates |  | RSF Note:
| 2 | 5 | 4.01 |  | 2.71 | 40 |  | 4.85 |  |  | Chemcial House | -
| 3 | 10 | 3.53 |  | 2.71 | 30 |  | 4.01 |  |  | CH&Chlorinator Room | -
|  | 5 | -0.48 |  | 3.09 | 20 |  | 3.53 |  |  | Bridge | Clariflucculator bridge including sludge srcapping arrangement shall be with stainless steel of Grade 304 for chemical resistance and durability are to be provided as per SSR 2011-2012.
|  | 0 | 0 |  | 3.53 | 10 |  | 3.09
|  | 5 | 4.01 |  | 4.01 | 5 |  | 2.71 |  |  | Capcity | Side wall | Rec Stag
[5 empty] | 4.85 | 2 |  | 2.71
[8 empty] | 20% | OHSR Rates |  | 10000 | 2.5 | 9,6
[8 empty] | 65.56 |  |  | 15000 | 2.5 | 9,6 | E) Deduct for staging below 10 Mts by .05 Paise per Lt |  |  |  | -2000
| Capacity | Staging | Inlet LPM |  |  |  |  | 45.09 |  |  | 20000 | 2 | 9,6
| 20000 | 9 | 42 |  |  |  |  | 44.31 |  |  | 40000 | 2.4 | 9.55,12.70 | E) Deduct for staging below 10 Mts by .05 Paise per Lt |  |  |  | 1200
| 40000 | 9.55 | 84 |  |  |  |  | 39.22 |  |  | 60000 | 2.5 | 12.90,9.75
| 60000 | 9.65 | 125 |  |  |  |  | 29.76 |  |  | 90000 | 3.15 | 12.75,9.60
| 90000 | 9.5 | 188 |  |  |  |  | 28.043 |  |  | 120000 | 3.75 | 12.75,9.60
| 120000 | 9.5 | 250 |  |  |  |  | 26.786 |  |  | 150000 | 4.55 | 12.90,9.75
| 150000 | 9.6 | 313 |  |  |  |  | 25.97 |  |  | 200000 | 3.9 | 13.05,9.90
| 200000 | 9.75 | 417 |  |  |  |  | 24.05 |  |  | 250000 | 4.55 | 13.20,10.05
| 250000 | 9.9 | 521 |  |  |  |  | 23.31 |  |  | 300000
| Inlet LPM | 125 | [5 empty] | 22.57 |  |  | 350000
| Outlet LPM | 250
| LPM | DIA |  | Dia | 0.6 | 0.9 | 2 | Duckfoot | Bellmouth | CI Sluicevalve With Conveyacne of 10% | 90o D/f bend | Tailpices | Semicircular Bend | DI Sluicevalve With Conveyacne of 5%
| 0 | 80 |  | 80 | 1420.936 | 1858.714 | 3463.9 | 1547.7 | 515.9 | 11025 | 958.1 | 1148.25 | 1842.5 | 9019.5
| 166 | 80 |  | 100 | 1742.268 | 2303.862 | 4363.04 | 1916.2 | 663.3 | 12368 | 1252.9 | 1432.73 | 2579.5 | 11897.55
| 167 | 100 |  | 125 | 2244.902 | 2976.743 | 5660.16 | 2653.2 | 884.4 | 15843 | 1695.1 | 1854.29 | 3316.5
| 271 | 100 |  | 150 | 2827.132 | 3746.908 | 7119.42 | 3463.9 | 1105.5 | 19473 | 2284.7 | 2333.34 | 4790.5 | 18734.1
| 272 | 125 |  | 200 | 4028.442 | 5357.253 | 10229.56 | 5453.8 | 1695.1 | 28613 | 3611.3 | 3343.03 | 7370 | 31131.45
| 440 | 125 |  | 250 | 5385.996 | 7194.594 | 13826.12 | 8180.7 | 2284.7 | 36488 | 5306.4 | 4501.6 | 11792 | 43117.2
| 441 | 150 |  | 300 | 6873.262 | 9219.133 | 17820.66 | 11497.2 | 3316.5 | 67740 | 7370 | 5782.5 | 15477 | 65165.1
| 654 | 150 |  | 350 | 8703.97 | 11655.655 | 22478.5 | 15771.8 | 4274.6 | 94238 | 10096.9 | 7303.67 | 25058 | 197300.25
| 655 | 200 |  | 400 | 10639.332 | 14234.418 | 27416.4 | 20709.7 | 5896 | 120488 | 13339.7 | 8914.75 | 20267.5 | 206937.15
| 1223 | 200 |  | 450 | 12617.44 | 16973.11 | 32943.9 | 25795 | 6854.1 | 197925 | 16656.2 | 10664.39 | 0 | 0
| 1224 | 250 |  | 500 | 14871.186 | 19941.009 | 38530.36 | 32870.2 | 8844 | 253050 | 21373 | 12505.42 | 0 | 0
| 1986 | 250 |  | 600 | 20039.03 | 26815.745 | 51663.7 | 49157.9 | 14813.7 | 358050 | 32575.4 | 16796.23 | 0 | 0
| 1987 | 300
| 2952 | 300
| 2953 | 350
| 4128 | 350
| 4129 | 400
| 5518 | 400
| 5519 | 450
| 7129 | 450
| 7130 | 500
| 8964 | 500
| 8965 | 600
| 13324 | 600
SSTank | 220857.6 |  | 195993.6
| 0 |  | 0
| 220857.6 | Cum | 195993.6 | Cum
| 88343.04 | Cum | 78397.44 | Cum
| 309200.64 | Cum | 274391.04 | Cum
| 309200.64 | Cum | 274391.04 | Cum
| 309200.64 |  | 274391.04
| 583760 |  | 518048
| 892960.64 |  | 792439.04
| 16 |  | 16
| 3797 |  | 3369
| 3.6451 |  | 3.2342
| Intake well cum pump house @ Canal |  |  |  | @ SSTank | [5 empty] | Canal |  | SSTank |  | Intake Well at SSTank
| Side wall thickness |  |  | 0.15 | 0.2 |  |  | Canal | Dia | Total depth | 3.1 | 3 | 3.25 | 3 | Total depth | 3.25 | 3 |  | Dia
| Ring beam depth |  |  | 0.3 | 0.45 |  |  |  | 350 | 2st mattu | 0.1 | 0.1 | 0.25 | 0.25 | 2st mattu | 0.25 | 0.25 |  | 300
| Ring beam breadth |  |  | 1.65 | 1.7 |  | 2 | 1 | 22479 | 3 rd mattu | 0 | 0 | 0 | 0 | 3 rd mattu | 0 | 0 | 2mts | 1 | 13826
| Pump house side wall thickness |  |  | 0.1 | 0.1 |  | 0.9 | 2 | 23311 | 4 th mattu | 0 | 0 | 0 | 0 | 4 th mattu | 0 | 0 | 0.90 Mts | 5 | 35973
| Bottom slab thickness |  |  | 0.15 | 0.2 |  | 0.6 | 1 | 8704 | [8 empty] | 0.60 Mts | 2 | 10772
| Top Slab Thickness |  |  | 0.1 | 0.1 |  | Duck foot bend | 1 | 15772 | [8 empty] | Bell Mouth | 1 | 2285
| Infiltration well | [5 empty] | Circular bend | 1 | 25058 | [8 empty] | Duck foot bend | 1 | 8181
| Side wall thickness |  |  | #REF! |  |  |  | Cost | 95324 | [9 empty] | Sum | 71037
| Infiltration well dia |  |  | #REF! | Curb Centreing
| Floor slab thickness |  |  | #REF!
Valve Chambers
| Side Wall |  |  | 0.1 |  | 0.9 | <150 mm
[6 empty] | 1.05 | 150-300 mm
[6 empty] | 1.2 | 300-450 mm
[6 empty] | 1.5 | 450-600 mm
OHBR
| Total depth | 3.65 | 3 |  | OHSR | 25.25 |  |  | Stair case | 30
| 2st mattu | 0.65 | 0.65 |  | Staging | 25.25 | 27 |  | Staging | 30 | 30
| 3 rd mattu | 0 | 0 |  | 15 | 1 |  |  | 15 | 1
| 4 th mattu | 0 | 0 |  | 15.005 | 9 |  |  | 15.005 | 9
[5 empty] | 18 | 9 |  |  | 18 | 9 | 27 | Flat slab
[5 empty] | 18.005 | 15 |  |  | 18.005 | 15
[5 empty] | 21 | 15 |  |  | 21 | 15
[5 empty] | 21.005 | 21 |  |  | 21.005 | 21
[5 empty] | 24 | 21 |  |  | 24 | 21
[5 empty] | 24.005 | 27 |  |  | 24.005 | 27
[5 empty] | 27 | 27 |  |  | 27 | 27
[5 empty] | 27.005 | 30 |  |  | 27.005 | 30
| Shaft |  |  |  | Shaft | 30
| Total depth | 3.1 | 3 |  | Staging | 30 | 30
| 2st mattu | 0.1 | 0.1 |  | 15 | 1
| 3 rd mattu | 0 | 0 |  | 15.005 | 9
| 4 th mattu | 0 | 0 |  | 18 | 9
[5 empty] | 18.005 | 15
| Shaft side wall thickness Below G.L |  |  | 0.3 | 21 | 15
| Shaft side wall thickness above G.L |  |  | 0.2 | 21.005 | 21
| Bottom Doome |  |  | 0.3 | 24 | 21
| Bottom ring Beam |  | 0.3 | 0.4 | 24.005 | 27
| conical sude wall |  |  | 0.2 | 27 | 27
| Top ring Beam |  | 0.3 | 0.4 | 27.005 | 30
| Inner shaft side wall |  |  | 0.15
| Inner shaft flat slab |  |  | 0.15
| top doome |  |  | 0.125
Collection Well Girder
[7 empty] | 450 | 72.4
| Total depth | 5.7 | 3 |  |  | ISMB | Wt
| 2st mattu | 2.7 | 2.7 |  |  | 100 | 11.5
| 3 rd mattu | 0 | 0 |  |  | 125 | 13
| 4 th mattu | 0 | 0 |  |  | 150 | 14.9 |  |  | 6 | 9.2 |  | 5-8mt | 1
[6 empty] | 175 | 19.3 |  | Thickness | Wt |  |  | 8-11mt | 2
| Side wall thickness |  | 1st step | 0.45 |  | 200 | 25.4 |  | 6 | 9.2 |  |  | 11-14mt | 3
|  |  | 2nd step | 0.4 |  | 225 | 31.2 |  | 8 | 12.1 |  |  | 14-17mt | 4
|  |  | 3rd step | 0.35 |  | 250 | 37.3 |  | 10 | 14.9 |  |  | 17-20mt | 5
|  |  | 4th step | 0.3 |  | 300 | 44.2 |  | 12 | 17.7 |  |  | 20-23mt | 6
|  |  | 5th step | 0.275 |  | 350 | 52.4
| Floor Slab thickness |  |  | 0.2 |  | 400 | 61.6
| Pump House side wall |  |  | 0.15 |  | 450 | 72.4
| Ring beam depth |  |  | 0.4 |  | 500 | 86.9
| Ring beam breadth |  |  | 1.65 |  | 550 | 103.7
| Top Slab Thickness |  |  | 0.15 |  | 600 | 122.6
Sump Rectangle
| Side Wall thickness-1st step |  | 0.2
| Side Wall thickness-2nd |  | 0.15

## Lead
Lead statement
2016-17
CPWS SCHEME TO DISTRICT
[8 empty] | Municipal allowence |  | 20% |  |  |  |  | 0.024 | 50 | 2083.3333
Sl.No | Description of material | Name of the Quarry | lead (km) | Initial cost | Conveyance-Excluding 13.615% | Stacking | Blasting charges | Machine crushing | seignorage/1.13615 | Total
1 | 40mm size HBG (SS5) |  | 50 | 845 | 692.25 |  |  |  | 44.0083 | 1581.2583 |  |  |  |  | 0.0405 | 20 | 493.8272
2 | 20mm size HBG metal |  | 50 | 1210 | 692.25 |  |  |  | 44.0083 | 1946.2583 |  |  |  |  | 0.054 | 23 | 425.9259 | 919.7531
3 | CR Stone |  | 30 | 288 | 510.94 |  |  |  | 44.0083 | 842.9483 | [7 empty] | 459.8765
4 | RR Stone |  | 30 | 252 | 400.74 |  |  |  | 44.0083 | 696.7483 |  | loading | deduct |  | 0.015 | 23 | 1533.3333
5 | Bond stone |  | 30 | 1360.95 | 510.94 |  |  |  | 44.0083 | 1915.8983 |  |  |  | 1335.4701 | 0.032813 | 39 | 1188.5714 | 2721.9048
6 | Sand for concrete items |  | 20 | 610 | 365.53 |  |  |  | 35.2066 | 1010.7366 | [5 empty] | old one |  | 1360.9524
7 | Sand for mortar |  | 20 | 677 | 365.53 |  |  |  | 35.2066 | 1077.7366
8 | Sand for filling |  | 5 | 460 | 201.82 |  |  |  | 35.2066 | 697.0266
9 | Bricks |  | 5 | 5200 | 303.57 |  |  |  | 33.8864 | 5537.4564 |  | deduct loading
10 | Cement (Ananthapuramu district) |  |  | 6400 | [5 empty] | 6400 | 281 | 5620 | Ananthapuramu
11 | Steel |  |  | 42000 | [5 empty] | 42000 |  | ssr | 6400
12 | Steel I Beams |  |  | 45000 | [5 empty] | 45000
13 | 6 mm size HBG metal |  | 50 | 735 | 692.25 |  |  |  | 44.0083 | 1471.2583 |  | 532 | 133
14 | 12mm size HBG metal |  | 50 | 1097 | 692.25 |  |  |  | 44.0083 | 1833.2583 |  |  | 735
15 | 10mm size HBG metal |  | 50 | 935 | 692.25 |  |  |  | 44.0083 | 1671.2583
16 | uncoursed rubble stone |  | 30 | 318 | 400.74 |  |  |  | 44.0083 | 762.7483 |  | loading deduct
17 | Gravel |  | 7 | 103 | 349.33 |  |  |  | 19.3636 | 471.6936
18 | Shabad stone |  | 20 | 235 | 17.37 |  |  |  | 2.2004 | 254.5704 |  | loading | deduct | 2.5
19 | Stone chips |  | 30 | 350 | 400.74 |  |  |  | 44.0083 | 794.7483
20 | Graded Metal ( 40mm to 20mm) |  | 50 | 1145 | 692.25 |  |  |  | 44.0083 | 1881.2583
21 | Present Pig Iron Cost as per BOC |  | 26000
22 | Present Coke Cost as per SSR |  | 36570
This is to certify that the leads are correct to the best of my knowledge

## Data
CPWS SCHEME TO DISTRICT
DATA SHEET
Datas-SSR -2015-16
[7 empty] | MA | 20% | [5 empty] | MA | 20%
[7 empty] | Overheads & C.Profit | 13.61%
| 1 | Earthwork in excavation for structures as per drawing and technical specifications Clause 305.1 including setting out, construction of shoring and bracing, removal of stumps and other deleterious material and disposal upto a lead of 50 m, dressing of sides and bottom and backfilling in trenches with excavated suitable material as per Technical Specification 305 MORD / 304 MORTH
ordianry gravelly soils for foundations
|  | 1 | cum | Initial rate | (3.64*295/10) |  |  | 116.48 | R&B.Ch.11/1
|  |  |  | Municipal allowance |  | 20% |  | 23.3
|  |  |  | Overheads & C.Profit |  | 13.61% |  | 19.031
[5 empty] | Total rate per 1cum |  |  | 158.8
|  |  | For 3m to 6m |  | (4.68*295/10)
|  | 1 | Cum | Initial cost | 149.76 | 1 | Cum | 149.76
|  |  |  | Municipal allowance | 20% |  |  | 29.952
|  |  |  | Overheads & cp |  | 13.61% |  | 24.4678
[7 empty] | Total | 204.2
|  |  | For above 6m depth |  | (6.24*295/10)
|  |  | 1 cum | Intial cost |  |  |  | 199.68 | R&B.Ch.11/2/A
|  |  |  | Municipal allowance | 20% |  |  | 39.936
|  |  |  | Overheads & C.Profit |  | 13.61% |  | 32.6237
[7 empty] | Total | 272.2
| 2 | Sand filling in basement with watering and tamping etc. complete.
|  | 1 | cum | cost of sand @ | Rs. | 697.0266 | per cum | 697.0266
|  | 1 | cum | Labour charges |  |  |  | 106.9 | R&B.Ch.11/2/A
|  |  |  | Municipal allowance |  | 20% |  | 21.38
|  |  |  | Overheads & cp |  | 13.61% |  | 112.3655
[5 empty] | Total rate per cum Rs. |  |  | 937.7
| 3 | Cement concrete (1:4:8)prop using 40 mm gauge HG metal including cost &conveyance
of all materials and labour charges ,seigniorage charges using concret mixer etc complete
|  | 162 | kg | Cement | Rs. | 6400 | cum | 1036.8
|  | 0.9 | cum | Coarse aggregate 40 mm | Rs. | 1581.2583 | cum | 1423.1324
|  | 0.45 | cum | Sand for concrete | Rs. | 1010.7366 | each | 454.8315
|  | 1.2 | kl | Water (including for curing) | Rs. | 77 | each | 92.4 | bldg.13
|  | 1 | hour | Concrete Mixer 10 / 7 cft (0.2 / 0.8 cum) capacity | Rs. | 338.6 | each | 338.6
|  | 0.1 | day | Mason 1st class | Rs. | 420 |  | 42
|  | 1.39 | day | Mazdoor (unskilled) | Rs. | 320 | Cum | 444.8
|  |  |  | Water Charges 1% |  |  |  | 4.868
|  |  |  | Municipal allowance |  | 20% |  | 97.36
|  |  |  | Overheads & cp |  | 13.61% |  | 535.7219
[7 empty] | Total Rs. | 4470.5
| 4 | Cement concrete (1:2.5:5)prop using 40 mm,0.050mm,10mm gauge HG metal including cost &conveyance | [5 empty] | M15 Grade
of all materials and labour charges ,seigniorage charges using concret mixer etc complete
|  | 275 | kg | Cement | Rs. | 6400 | cum | 1760
|  | 0.54 | cum | Coarse aggregate 40 mm | Rs. | 1581.2583 | cum | 853.8795
|  | 0.27 | cum | Coarse aggregate 20 mm | Rs. | 1946.2583 | cum | 525.4897
|  | 0.09 | cum | Coarse aggregate 10 mm | Rs. | 1671.2583 | cum | 150.4132
|  | 0.48 | cum | Sand for concrete | Rs. | 1010.7366 | each | 485.1536
|  | 1.2 | kl | Water (including for curing) | Rs. | 77 | each | 92.4 | bldg.13
|  | 1 | hour | Concrete Mixer 10 / 7 cft (0.2 / 0.8 cum) capacity | Rs. | 338.6 | each | 338.6
|  | 0.1 | day | Mason 1st class | Rs. | 420 | MT | 42
|  | 1.39 | day | Mazdoor (unskilled) | Rs. | 320 | Cum | 444.8
|  |  |  | Municipal allowance |  | 20% |  | 97.36
|  |  |  | Overheads & cp |  | 13.61% |  | 652.1716
[7 empty] | Total Rs. | 5442.3
| 5 | Construction of Randam rubble stone masonry in CM(1:6) 2nd sort including cost and
conveyance of all materials and labour charges ,seigniorage charges etc complete.
|  | 79.2 | kg | Cement | Rs. | 6400 | kg | 506.88
|  | 0.44 | cum | CR Stone | Rs. | 842.9483 | cum | 370.8972
|  | 0.5 | cum | Rough Stone | Rs. | 696.7483 | cum | 348.3741
|  | 0.16 | cum | Bond Stones 7Nos 0.24 x 0.24 x 0.39 = 0.16cum | Rs. | 1915.8983 | cum | 306.5437 | bldg.44
|  | 0.33 | cum | Sand for Mortar | Rs. | 1077.7366 | cum | 355.6531
|  | 1.2 | day | Mason 1st class | Rs. | 420 | day | 504
|  | 2 | day | Mazdoor (unskilled) | Rs. | 320 | day | 640
|  |  |  | Municipal allowance |  | 20% |  | 228.8
|  |  |  | Overheads & cp |  | 13.61% |  | 444.0053
[5 empty] | Total rate per cum Rs. |  |  | 3705.2
| 6 | Construction of course rubble stone masonry in CM(1:6) 2nd sort including cost and
conveyance of all materials and labour charges ,seigniorage charges etc complete.
|  | 0.94 | cum | Intial cost of CR stone @ | Rs. | 842.9483 | cum | 792.3714
|  | 0.16 | cum | Bond Stones 7Nos 0.24 x 0.24 x 0.39 = 0.16cum | Rs. | 1915.8983 | cum | 306.5437
|  | 0.32 | cum | Sand for Mortar | Rs. | 1077.7366 | cum | 344.8757
|  | 1.5 | nos. | masons 1st class @ | Rs. | 420 | each | 630 | bldg.39
|  | 2.32 | nos. | man and woman mazdoor @ | Rs. | 320 | each | 742.4
|  | 0.0768 | MT | cost of cement @ | Rs. | 6400 | MT | 491.52
|  |  |  | Municipal allowance |  | 20% |  | 274.48
|  |  |  | Overheads & cp |  | 13.61% |  | 487.7153
[5 empty] | Total rate per cum Rs. |  |  | 4069.9
| 7 | Construction of super stucture with brick masonary in (1:6) using 2nd class bricks including
cost and conveyance of all materials,labour charges and seign. charges etc. complete.
|  | 520 | nos. | cost of bricks | Rs. | 5537.4564 | per 1000 | 2879.4773
|  | 0.21 | cum | Sand for Mortar | Rs. | 1077.7366 | cum | 226.3247
|  | 0.24 | nos. | brick layer 1st class @ | Rs. | 420 | each | 100.8
|  | 0.56 | nos. | brick layer 2nd class @ | Rs. | 375 | each | 210 | bldg.30/iv
|  | 1.89 | nos. | man and woman mazdoor @ | Rs. | 320 | each | 604.8
|  | 0.0504 | MT | cost of cement @ | Rs. | 6400 | MT | 322.56
|  |  |  | Municipal allowance |  | 20% |  | 183.12
|  |  |  | Overheads & cp |  | 13.61% |  | 616.3622
[5 empty] | Total rate per cum Rs. |  |  | 5143.4
| 8 | Cement concrete(1:1.5:3) prop using 20mm gauge HG metal including cost and conveyance
of all materials and labour charges ,seign. charges etc.complete.
FOUNDATIONS, PLINTH, PEDESTALS (Below Plinth)
|  | 0.9 | cum | 20mm HBG graded metal | Rs. | 1946.2583 | cum | 1751.6324
|  | 0.45 | cum | Sand for concrete | Rs. | 1010.7366 | cum | 454.8315
|  | 400 | Kgs | Cement | Rs. | 6400 | Kgs | 2560
|  | 0.133 | day | 1st Class Mason | Rs. | 420 | day | 55.86
|  | 0.267 | day | 2nd Class Mason | Rs. | 375 | day | 100.125
|  | 3.6 | day | Mazdoor (Both Men and Women) | Rs. | 320 | day | 1152
|  | 1 | hour | Concrete Mixer 10 / 7 cft (0.2 / 0.8 cum) capacity | Rs. | 338.6 | hour | 338.6 | bldg.21-A
|  | 0.133 | Liters | Cost of Diesel for Miller | Rs. | 57 | Liters | 7.581
|  | 0.667 | Liters | Cost of Petrol for Vibrator |  | 69 | Liters | 46.023
|  | 1.2 | kl | Water (including for curing) |  | 77 | kl | 92.4
|  |  |  | Municipal allowance |  | 20% |  | 261.597
|  |  |  | Overheads & cp |  | 13.61% |  | 928.63
[5 empty] | Total rate per cum |  |  | 7749.3
| 9 |  | COLUMNS, LINTELS, WATER TANKS, RCC WALLS IN BUILDINGS
|  | 0.9 | cum | 20mm HBG graded metal |  | 1946.2583 | cum | 1751.6324
|  | 0.45 | cum | Sand for concrete |  | 1010.7366 | cum | 454.8315
|  | 400 | Kgs | Cement |  | 6400 | Kgs | 2560
|  | 0.167 | day | 1st Class Mason |  | 420 | day | 70.14
|  | 0.167 | day | 2nd Class Mason |  | 375 | day | 62.625
|  | 4.7 | day | Mazdoor (Both Men and Women) |  | 320 | day | 1504 | bldg.21-B
|  | 1 | hour | Concrete Mixer 10 / 7 cft (0.2 / 0.8 cum) capacity |  | 338.6 | hour | 338.6
|  | 1.2 | kl | Water (including for curing) |  | 77 | kl | 92.4
|  |  |  | Municipal allowance |  | 20% |  | 327.353
|  |  |  | Overheads & cp |  | 13.61% |  | 975.05
8136.6
| 10 |  | RCC SLABS, BEAMS
|  | 0.9 | cum | 20mm HBG graded metal |  | 1946.2583 | cum | 1751.6324
|  | 0.45 | cum | Sand for concrete |  | 1010.7366 | cum | 454.8315
|  | 400 | Kgs | Cement |  | 6400 | Kgs | 2560
|  | 0.067 | day | 1st Class Mason |  | 420 | day | 28.14
|  | 0.133 | day | 2nd Class Mason |  | 375 | day | 49.875
|  | 2.5 | day | Mazdoor (Both Men and Women) |  | 320 | day | 800 | bldg.21-C
|  | 0.267 | hour | Concrete Mixer 10 / 7 cft (0.2 / 0.8 cum) capacity |  | 338.6 | hour | 90.4062
|  | 1.2 | kl | Water (including for curing) |  | 77 | kl | 92.4
|  |  |  | Municipal allowance |  | 20% |  | 175.603
|  |  |  | Overheads & cp |  | 13.61% |  | 817.29
6820.2
| 11 |  | Pump House Roof Slab
VRCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for round slab of
|  |  | 150 | mm thick
|  | 1.5 | Cum | Cost of VCC (1:1.5:3) | 6820.2 | 1 | cum | 10230.3
|  | 10 | sqm | Centering charges | 389 | 1 | Sqm | 3890
|  |  |  | Municipal allowance | 20% |  |  | 194.5
|  |  |  | Overheads & cp |  | 13.61% |  | 556.1047
Sundies
[7 empty] | Total 10sqmt | 14870.9
Pump House ,W.Quarter
| 12 | VRCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for floor slab of
|  |  | 125 | mm thick
|  | 1.25 | Cum | Cost of VCC (1:1.5:3) | 6820.2 | 1 | cum | 8525.25
|  | 10 | sqm | Centering charges | 389 | 1 | Sqm | 3890
|  |  |  | Municipal allowance | 20% |  |  | 194.5
|  |  |  | Overheads & cp |  | 13.61% |  | 556.1047
Sundies
[7 empty] | Total 10sqmt | 13165.9
| 13 | Prop | Item | Basic Rate & labour Including Cont Profit | Centering Charges | Add MAand cont profit 13.615% | Total Rate | Per
| (1:1.5:3) | Footings |  | 7749.3 | 750 | 144.7181 | 8644 | /1Cum
| (1:1.5:3) | Columns |  | 8136.6 | 2041 | 393.8263 | 10571.4 | /1Cum
| (1:1.5:3) | Columns above 3.66 m |  | 8136.6 | 2381 | 459.4318 | 10977 | /1Cum
| (1:1.5:3) | Beams |  | 6820.2 | 3428 | 661.4583 | 10909.7 | /1Cum
| (1:1.5:3) | Beams above 3.66m height |  | 6820.2 | 4572 | 882.2017 | 12274.4 | /1Cum
| (1:1.5:3) | Lintels |  | 8136.6 | 2344 | 452.2924 | 10932.9 | /1Cum
| (1:1.5:3) | Sun shades 0.6m Width |  | 8136.6 | 410 | 79.1126 | 8625.7 | /1Cum
| (1:1.5:3) | Roof slab 150mm thick |  | 6820.2 | 389 | 75.0605 | 7284.3 | /1Cum
| (1:1.5:3) | Roof slab 150-300mm thick |  | 6820.2 | 399 | 76.99 | 7296.2 | /1Cum
| (1:1.5:3) | Roof slab above 300.0mm thick above 3.66m height |  | 6820.2 | 818 | 157.8392 | 7796 | /1Cum
| (1:1.5:3) | Bed blocks |  | 7749.3 | 305 | 58.852 | 8113.2 | /1Cum
| (1:1.5:3) | Pedestrals |  | 7749.3 | 1068 | 206.0786 | 9023.4 | /1Cum
| 14 | Cost of CM(1:3) prop including cost and conveyance of all materials and labour
charges etc., complete.
|  | 0.48 | cum | Cost of cement @ | Rs. | 6400 | MT | 3072
|  | 1.05 | cum | cost of sand @ | Rs. | 1077.7366 | cum | 1131.6234
|  | 0.2 | cum | mixing charges @ | Rs. | 320 | cum | 64 | bldg.4
|  |  |  | Municipal allowance |  | 20% |  | 12.8
[5 empty] | Total rate per cum Rs. |  |  | 4280.4
| 15 | Cost of CM(1:4) prop including cost and conveyance of all materials and labour
charges etc., complete.
|  | 0.36 | cum | Cost of cement @ | Rs. | 6400 | MT | 2304
|  | 1.05 | cum | cost of sand @ | Rs. | 1077.7366 | cum | 1131.6234
|  | 0.2 | cum | mixing charges @ | Rs. | 320 | cum | 64 | bldg.5
|  |  |  | Municipal allowance |  | 20% |  | 12.8
[5 empty] | Total rate per cum Rs. |  |  | 3512.4
| 16 | Cost of CM(1:5) prop including cost and conveyance of all materials and labour
charges etc., complete.
|  | 0.288 | cum | Cost of cement @ | Rs. | 6400 | MT | 1843.2
|  | 1.05 | cum | cost of sand @ | Rs. | 1077.7366 | cum | 1131.6234
|  | 0.2 | cum | mixing charges @ | Rs. | 320 | cum | 64 | bldg.6
|  |  |  | Municipal allowance |  | 20% |  | 12.8
[5 empty] | Total rate per cum Rs. |  |  | 3051.6
| 17 | Cost of CM(1:6) prop including cost and conveyance of all materials and labour
charges etc., complete.
|  | 0.24 | cum | Cost of cement @ | Rs. | 6400 | MT | 1536
|  | 1.05 | cum | cost of sand @ | Rs. | 1077.7366 | cum | 1131.6234
|  | 0.2 | cum | mixing charges @ | Rs. | 320 | cum | 64 | bldg.7
|  |  |  | Municipal allowance |  | 20% |  | 12.8
[5 empty] | Total rate per cum Rs. |  |  | 2744.4
| 18 | Flush pointing with CM(1:3) prop for stone/brick masonry including cost and conveyance of all
materials,labour charges and seign. chargesetc. complete.
|  | 0.03 | cum | cost of sand @ | Rs. | 1077.7366 | cum | 32.3321
|  | 0.5 | nos. | masons 2nd class @ | Rs. | 375 | each | 187.5
|  | 0.74 | nos. | man and woman mazdoor @ | Rs. | 320 | each | 236.8
|  | 0.0144 | MT | cost of cement @ | Rs. | 6400 | MT | 92.16 | bldg.49
|  |  |  | Municipal allowance |  | 20% |  | 84.86
|  |  |  | Overheads & cp |  | 13.61% |  | 86.2717
[5 empty] | Total rate per 10 sqm |  |  | 719.9
| 19 | Plastering with CM(1:3) prop 20mm thick to brick wall including cost&coveyance of all
|  | materials, lalbour charges,seign.charges etc.complete. |  |  |  |  | (1:3)-20mm | (1:5)-20mm
|  | 0.21 | Cum | Cost of CM(1:3) | 4280.4 | cum | 898.884 | 640.836
|  | 0.94 | Nos. | Mason 2nd class | 375 | cum | 352.5 | 352.5
|  | 1.6 | Nos. | Man Mazdoor | 320 | each | 512 | 512 | bldg.60
|  |  |  | Municipal allowance | 20% |  | 172.9 | 172.9
|  |  |  | Overheads & cp | 13.61% |  | 263.6251 | 234.953
[5 empty] | Total rate per 10 sqm |  | 2199.9 | 1913.2
| 20 | Impervous coat with Plastering in CM(1:3) prop 12mm thick including cost&coveyance of all
|  | materials lalbour charges,seign.charges etc.complete for wearing coat. |  |  |  |  | 12mm thick | 20mm thick
|  | 0.15 | cum | Cost of CM(1:3) | 4280.4 |  | 642.06 | 898.884
|  | 0.6 | nos. | mason 1st class @ | 420 |  | 252 | 394.8 | bldg.53,112
|  | 0.96 | nos. | man and woman mazdoor @ | 320 |  | 307.2 | 512
|  | 1.5 | Kg | accoproof chemical @ | 75 |  | 112.5 | 150
|  |  |  | Municipal allowance | 20% |  | 111.84 | 181.36
|  |  |  | Overheads & cp | 13.61% |  | 194.0954 | 299.1862
[5 empty] | Total rate per 10 Sqm |  | 1619.7 | 2436.2
| 21 | Impervous coat with Plastering in CM(1:3) prop 12mm thick including cost&coveyance of all
materials lalbour charges,seign.charges etc.complete for wearing coat.above 3.0m height
|  |  |  | Rate up to 3.0m heighr |  |  |  | 1619.7
|  |  |  | add lift charges |  |  |  | 67
|  |  |  | Municipal allowance |  | 20% |  | 3.35
|  |  |  | Overheads & cp |  | 13.61% |  | 9.5782
[5 empty] | Total rate per 10 Sqm |  |  | 1699.6
| 22 | Flooring with CM(1:3) prop 20 mm thick over bed of 100 mm thick,CC (1:4:8) prop
using 40mm HG metal including cost and conveyance of all materials and seignorage
charges etc., complete.
|  | 1 | Cum | Cost of CC (1:4:8) prop. | Rs. | 4470.5 | /1Cum | 4470.5
|  | 10 | sqm | Cost of CM(1:3) 20mm thick | Rs. | 2199.9 | /10sqmt | 2199.9 | bldg.85
[5 empty] | Total rate per 10 sqm |  |  | 6670.4
| 23 | Plastering with 12mm thick with sponge finish first coat in CM(1:5) Prop 8mm
thick and second coat in CM(1:3) prop 4mm thick including cost and conveyance
of all materials and labour charges etc., complete
|  | 0.11 | cum | Cost of CM(1:5) Prop 8mm | Rs. | 3051.6 | /1Cum | 335.676
|  | 0.04 | cum | Cost of CM(1:3) Prop 4mm | Rs. | 4280.4 | /1Cum | 171.216
|  | 0.63 | nos. | Mason 1st class @ | Rs. | 420 | /each | 264.6
|  | 1.47 | nos. | Mason 2nd class @ | Rs. | 375 | /each | 551.25 | bldg.62
|  | 3.9 | nos. | man and woman mazdoor @ | Rs. | 320 | /each | 1248
|  |  |  | Municipal allowance |  | 20% |  | 412.77
|  |  |  | Overheads & cp |  | 13.61% |  | 406.2052
[5 empty] | Total rate per 10 Sqm |  |  | 3389.7
| 24 | Plastering with 12mm thick with sponge finish first coat in CM(1:5) Prop 8mm
thick and second coat in CM(1:3) prop 4mm thick including cost and conveyance
of all materials and labour charges etc., complete above 3.0m height
|  |  |  | Rate up to 3.0m height |  |  |  | 3389.7
|  |  |  | Lift charges |  |  |  | 67
|  |  |  | Municipal allowance |  | 20% |  | 3.35
|  |  |  | Overheads & cp |  | 13.61% |  | 9.5782
[5 empty] | Total rate per 10 Sqm |  |  | 3469.6
| 25 | Painting to new wood work with one primary coat including
cost and conveyance of all materials and labour charges etc. complete.
|  | 0.7 | ltr | wood primer | Rs. | 158 | /1 ltr | 110.6
|  | 0.7 | nos. | painters | Rs. | 420 | each | 294 | bldg.145
|  | 1% |  | Sundries including brushes, soap, putty etc., |  |  |  | 4.046
|  |  |  | Municipal allowance |  | 0.2 |  | 58.8
[5 empty] | Total rate per 10sqm |  |  | 467.4
| 26 | Painting to new wood work with synthetic enamel paint two coats over a primary coat including
cost and conveyance of all materials and labour charges etc. complete.
|  | 1 | 10sqm | cost of primary coat | Rs. | 467.4 | /1 ltr | 467.4
|  | 2.8 | litres | cost of paint | Rs. | 276 | /1 ltr | 772.8 | bldg.149-ii
|  | 1.2 | nos. | painters 1st class | Rs. | 480 | each | 576
|  | 1% |  | Sundries including brushes, soap, putty etc., |  |  |  | 13.488
|  |  |  | Municipal allowance |  | 20% |  | 115.2
|  |  |  | Overheads & cp |  | 13.61% |  | 264.7965
[5 empty] | Total rate per 10sqm |  |  | 2209.7
| 27 | White washing with white cement two coats including cost and conveyance of all materials
and labour charges etc complete.
|  | 2 | kg | cost of white cement | Rs. | 29 | /1kg | 58
|  |  |  | Gum, Conjee water or prickly pear juice including necessary firewood |  |  |  | 0.58
|  | 0.21 | nos. | Painter 1st class @ | Rs. | 480 | each | 100.8 | bldg.134
|  | 0.32 | nos. | man and woman mazdoor | Rs. | 320 | each | 102.4
|  |  |  | Sundries including brushes, soap, putty etc., |  |  |  | 2.6178
|  |  |  | Municipal allowance |  | 20% |  | 40.64
|  |  |  | Overheads & cp |  | 13.61% |  | 41.5309
[5 empty] | Total rate per 10sqm |  |  | 346.6
| 28 | Blue &bluff colour wash two coats to basement for 10 Sqm white wash with white cement
346.6
|  |  |  | Add 50% extra for colour |  |  |  | 173.3
0.01
[6 empty] | Total Rs. |  | 519.91
| 28 | Snowcem paint two coats including cost and conveyence
of all materials and labour charges etc.comp
|  | 3.5 | kg | Snowcem @ | Rs. | 53 | per kg | 185.5
|  | 0.5 | nos | Painter 1st class @ | Rs. | 480 | per each | 240
|  | 1.5 | nos | Mazdoor @ | Rs. | 320 | per each | 480
|  |  |  | Sundries including brushes, etc., |  |  |  | 9.055 | bldg.143
|  |  |  | Municipal allowance |  | 0.2 |  | 144
|  |  |  | Overheads & cp |  | 13.61% |  | 144.1223
[7 empty] | Total Rs. | 1202.7
| 29 | Cost of steel and its fabrication charges incl., bending, cost of binding wire etc., complete
|  | as per standard specification |  |  |  |  | steel | Steel beams
|  | 1.05 | MT | Cost of steel | 42000 |  | 44100 | 47250
|  | 6 |  | Binding wire | 70 | kg | 420
|  | bldg.26 |  | (b) Labour for cutting, bending, shifting to site, tying and placing in position
|  | 10 |  | Blacksmith / Bar bender | 420 | day | 4200 | 4200
|  | 10 |  | Mazdoor (Unskilled) | 320 | day | 3200 | 3200
|  |  |  | Municipal allowance | 20% |  | 1480 | 1480
|  |  |  | Overheads & cp |  | 13.61% | 7270.41 | 7642.0995
Sundries on Material
[6 empty] | Total Rs. | 60670.4 | 63772.1
| 30 | 1 sqm |  | Supply and fixing of Rolling shutter made of 80 x 1.25mm machine rolled CRCA laths, interlocked together through their entire length and jointed together at the ends by end locks, mounted on specially designed pipe shaft of 50mm dia nominal bore MS B class pipe with brackets, plates, guide channels, stoppers, bottom locking plates and arrangements for inside and out side locking with push pull operations including cost of hood cover and springs complete, painted with one coat of approved steel primer, locks, ball bearings, all accessories etc., complete for finished item of work as per special spn: 1108 etc., complete
|  |  |  | Initial rate | 1 | sqm | 2861 | 2861 | item as per bldg ssr 152
|  |  |  | Municipal allowance |  | 20% |  | 143.05
|  |  |  | Overheads & cp |  | 13.61% |  | 420.567
3424.6
| 30 | Plastering with CM (1:5) 12mm thick including cost and conveyance of all material, labour charges etc., complete
|  | 0.15 | Cum | Cost of CM(1:3) | 3051.6 | 1 | Cum | 457.74
|  | 0.6 | Nos. | Mason | 420 |  | Each | 252
|  | 0.96 | Nos. | Man Mazdoor | 320 |  | Each | 307.2
|  |  |  | Municipal allowance | 20% |  |  | 111.84
|  |  |  | Overheads & cp |  | 13.61% |  | 91.3621
[7 empty] | Total | 1220.1
Cement Mortar (1:3)
|  | 480 | Kgs | Cost of Cement | 6400 | 1 | Ton | 3072
|  | 1.05 | Cum | Sand (including 5% wastage) | 1077.7366 | 1 | Cum | 1131.6234
|  | 0.2 | day | mazdoor forMixing charges | 320 | 1 | day | 64
|  |  |  | Municipal allowance | 20% |  |  | 12.8
|  |  |  | Overheads & cp |  | 13.61% |  | 582.7797
4863.2
Cement Mortar (1:4)
|  | 360 | Kgs | Cost of Cement | 6400 | 1 | Ton | 2304
|  | 1.05 | Cum | Sand (including 5% wastage) | 1077.7366 | 1 | Cum | 1131.6234
|  | 0.2 | day | Mazdoor (unskilled) | 320 | 1 | day | 64
|  |  |  | Municipal allowance | 20% |  |  | 12.8
|  |  |  | Overheads & cp |  | 13.61% |  | 478.2165
3990.6
| 31 | Plain Cement concrete (1:3:6) using 40 mm metal with concrete mixture.
|  | 220 | kg | Cement | 6400 | 1 | Tonne | 1408
|  | 0.9 | cum | Coarse aggregate 40 mm | 1581.2583 | 1 | Cum | 1423.1324
|  | 0.45 | cum | Fine aggregate (Sand) | 1010.7366 | 1 | Cum | 454.8315
|  | 1.2 | kl | Water (including for curing) | 77 | 1 | Kl | 92.4
|  | 1 | hour | Concrete Mixer 10 / 7 cft (0.2 / 0.8 cum) capacity | 338.6 | 1 | Hour | 338.6
|  | 0.1 | day | Mason 1st class | 420 | 1 | day | 42
|  | 1.39 | day | Mazdoor (unskilled) | 320 | 1 | day | 444.8
|  |  |  | Water Charges 1% |  |  |  | 4.868
|  |  |  | Municipal allowance | 20% |  |  | 97.36
|  |  |  | Overheads & cp |  | 13.61% |  | 586.2608
Sundies
[7 empty] | Total | 4892.3
| 32 | Supply and placing of the Design Mix Concrete corresponding to IS 456 using WEIGH BATCHER / MIXER with 20mm size graded machine crushed hard granite metal (coarse aggregate) from approved quarry including cost and conveyance of all materials like cement, for M-30 grade | [6 empty] | M30 Grade (Design Mix)
FOUNDATIONS, PLINTH, PEDESTALS (Below Plinth)
|  | 0.8 | cum | 20mm HBG graded metal | 1946.2583 | 1 | cum | 1557.0066
|  | 0.4 | cum | Sand | 1010.7366 | 1 | cum | 404.2946
|  | 400 | Kgs | Cement | 6400 | 1 | Kgs | 2560
|  | 0.133 | day | 1st Class Mason | 420 | 1 | day | 55.86
|  | 0.267 | day | 2nd Class Mason | 375 | 1 | day | 100.125
|  | 4.6 | day | Mazdoor (Both Men and Women) | 320 | 1 | day | 1472
|  | 1.333 | hour | Weigh Batcher hire charges | 556.8 | 1 | hour | 742.2144
|  | 0 | Liters | Cost of Diesel for Miller | 57 | 1 | Liters | 0
|  | 0 | Liters | Cost of Petrol for Vibrator | 69 | 1 | Liters | 0
|  | 1.2 | kl | Water (including for curing) | 77 | 1 | kl | 92.4
|  |  |  | Municipal allowance | 20% |  |  | 325.597
|  |  |  | Overheads & cp |  | 13.61% |  | 995.1881
[7 empty] | Total | 8304.7
| 33 |  | COLUMNS, LINTELS, WATER TANKS, RCC WALLS IN BUILDINGS
|  | 0.8 | cum | 20mm HBG graded metal | 1946.2583 | 1 | day | 1557.0066
|  | 0.4 | cum | Sand | 1010.7366 | 1 | day | 404.2946
|  | 400 | Kgs | Cement | 6400 | 1 | day | 2560
|  | 0.167 | day | 1st Class Mason | 420 | 1 | day | 70.14
|  | 0.167 | day | 2nd Class Mason | 375 | 1 | day | 62.625
|  | 5.6 | day | Mazdoor (Both Men and Women) | 320 | 1 | day | 1792
|  | 1.333 | hour | Weigh Batcher hire charges | 556.8 | 1 | day | 742.2144
|  | 1.2 | kl | Water (including for curing) | 77 | 1 | day | 92.4
|  |  |  | Municipal allowance | 20% |  |  | 384.953
|  |  |  | Overheads & cp |  | 13.61% |  | 1043.676
8709.3
| 34 |  | RCC SLABS, BEAMS
|  | 0.8 | cum | 20mm HBG graded metal | 1946.2583 | 1 | day | 1557.0066
|  | 0.4 | cum | Sand | 1010.7366 | 1 | day | 404.2946
|  | 400 | Kgs | Cement | 6400 | 1 | day | 2560
|  | 0.067 | day | 1st Class Mason | 420 | 1 | day | 28.14
|  | 0.133 | day | 2nd Class Mason | 375 | 1 | day | 49.875
|  | 3.077 | day | Mazdoor (Both Men and Women) | 320 | 1 | day | 984.64
|  | 0.308 | hour | Weigh Batcher hire charges | 556.8 | 1 | day | 171.4944
|  | 1.2 | kl | Water (including for curing) | 77 | 1 | day | 92.4
|  |  |  | Municipal allowance | 20% |  |  | 212.531
|  |  |  | Overheads & cp |  | 13.61% |  | 825.1
6885.5
| 35 | VRCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for floor slab for foundations
|  | 1 | Cum | Cost of VCC (1:1.5:3) | 8304.7 | 1 | Sqm | 8304.7
|  | 1 | Cum | Centering charges | 750 | 1 | Cum | 750
|  |  |  | Municipal allowance | 20% |  |  | 37.5
|  |  |  | Overheads & cp |  | 13.61% |  | 107.2181
Sundies
[7 empty] | Total | 9199.4
| 36 | VRCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for Haunch portion
|  | 1 | Cum | Cost of VCC (1:1.5:3) | 8304.7 | 1 | Sqm | 8304.7
|  | 1 | Cum | Centering charges | 750 | 1 | Cum | 750
|  |  |  | Municipal allowance | 20% |  |  | 37.5
|  |  |  | Overheads & cp |  | 13.61% |  | 107.2181
[7 empty] | Total | 9199.4
| 37 | VRCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for side wall of (Circular)
|  | Sump | 200 | mm thick | [5 empty] | 2 sides given
|  | 1 | Cum | Cost of CC (1:1.5:3) | 8709.3 | 1 | Cum | 8709.3
|  | 5 | Sqm | Centering charges | 1115 | 1 | Sqm | 5575
|  |  |  | Municipal allowance | 20% |  |  | 278.75
|  |  |  | Overheads & cp |  | 13.61% |  | 796.9881
[7 empty] | Total | 15360
|  |  | 300 | mm thick
|  | 1 | Cum | Cost of CC (1:1.5:3) | 8709.3 | 1 | Cum | 8709.3
|  | 3.3333 | Sqm | Centering charges | 1115 | 1 | Sqm | 3716.6667
|  |  |  | Municipal allowance | 20% |  |  | 185.8333
|  |  |  | Overheads & cp |  | 13.61% |  | 531.3254
[7 empty] | Total | 13143.1
|  |  | 250 | mm thick
|  | 1 | Cum | Cost of CC (1:1.5:3) | 8709.3 | 1 | Cum | 8709.3
|  | 4 | Sqm | Centering charges | 1115 | 1 | Sqm | 4460
|  |  |  | Municipal allowance | 20% |  |  | 223
|  |  |  | Overheads & cp |  | 13.61% |  | 637.5904
[7 empty] | Total | 14029.9
| 38 | VRCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for side wall of (Circular)
|  | Sump-Flat | 100 | mm thick
|  | 1 | Cum | Cost of CC (1:1.5:3) | 8709.3 | 1 | Cum | 8709.3
|  | 10 | Sqm | Centering charges | 1115 | 1 | Sqm | 11150
|  |  |  | Municipal allowance | 20% |  |  | 557.5
|  |  |  | Overheads & cp |  | 13.61% |  | 1593.9761
[7 empty] | Total | 22010.8
| 39 | RCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for Sump top slab
|  |  | 150 | mm thick |  |  |  | Sump-Flat
|  | 1.5 | Cum | Cost of CC (1:1.5:3) | 6885.5 | 1 | Cum | 10328.25
|  | 6.6667 | Sqm | Centering charges | 389 | 1 | Sqm | 2593.3333
|  |  |  | Municipal allowance | 20% |  |  | 129.6667
|  |  |  | Overheads & cp |  | 13.61% |  | 370.7364
[7 empty] | Total 10sqmt | 13422
|  |  | 125 | mm thick |  |  |  | Sump-Flat
|  | 1.25 | Cum | Cost of CC (1:1.5:3) | 6885.5 | 1 | Cum | 8606.875
|  | 8 | Sqm | Centering charges | 389 | 1 | Sqm | 3112
|  |  |  | Municipal allowance | 20% |  |  | 155.6
|  |  |  | Overheads & cp |  | 13.61% |  | 444.8837
[7 empty] | Total 10sqmt | 12319.4
| 40 | VRCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for side wall of (Circular)
| GLBR | Side Wall | 100 | mm thick
|  | 1 | Cum | Cost of CC (1:1.5:3) | 8709.3 | 1 | Cum | 8709.3
|  | 10 | Sqm | Centering charges | 1115 | 1 | Sqm | 11150
|  |  |  | Municipal allowance | 20% |  |  | 557.5
|  |  |  | Overheads & cp |  | 13.61% |  | 1593.9761
[7 empty] | Total | 22010.8
VRCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for top dome
|  | GLBR-Doome | 100 | mm thick
|  | 1 | Cum | Cost of CC (1:1.5:3) | 6885.5 | 1 | Cum | 6885.5
|  | 1 | cum | Centering charges (as per bldg SSR) | 6302 | 1 | cum | 6302
|  |  |  | Municipal allowance | 20% |  |  | 315.1
|  |  |  | Overheads & cp |  | 13.61% |  | 900.9182
[7 empty] | Total | 14403.5
VRCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for top ring beam of
Ring Beam
|  | 1 | Cum | Cost of CC (1:1.5:3) | 6885.5 | 1 | Cum | 6885.5
|  | 1 | Cum | Centering charges | 3428 | 1 | Cum | 3428
|  |  |  | Municipal allowance | 20% |  |  | 171.4
|  |  |  | Overheads & cp |  | 13.61% |  | 490.0583
[7 empty] | Total | 10975
VRCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for side wall of (Circular)
|  | GLBR-Flat | 100 | mm thick
|  | 1 | Cum | Cost of CC (1:1.5:3) | 8709.3 | 1 | Cum | 8709.3
|  | 10 | Sqm | Centering charges | 1115 | 1 | Sqm | 11150
|  |  |  | Municipal allowance | 20% |  |  | 557.5
|  |  |  | Overheads & cp |  | 13.61% |  | 1593.9761
[7 empty] | Total | 22010.8
RCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for GLBR top slab
|  |  | 150 | mm thick |  |  |  | GLBR-Flat
|  | 1.5 | Cum | Cost of CC (1:1.5:3) | 6885.5 | 1 | Cum | 10328.25
|  | 6.6667 | Sqm | Centering charges | 389 | 1 | Sqm | 2593.3333
|  |  |  | Municipal allowance | 20% |  |  | 129.6667
|  |  |  | Overheads & cp |  | 13.61% |  | 370.7364
[7 empty] | Total 10sqmt | 13422
|  | Intake-Canal | 150 | mm thick- Side Wall |  |  |  | Canal
|  | 1 | Cum | Cost of CC (1:1.5:3) | 8709.3 | 1 | Cum | 8709.3
|  | 6.6667 | Sqm | Centering charges | 1115 | 1 | Sqm | 7433.3333
|  |  |  | Municipal allowance | 20% |  |  | 297.3333
|  |  |  | Overheads & cp |  | 13.61% |  | 1052.5303
[7 empty] | Total | 17492.5
|  |  | 125 |  |  |  |  | Canal
|  | 1 | Cum | Cost of CC (1:1.5:3) | 8709.3 | 1 | Cum | 8709.3
|  | 8 | Sqm | Centering charges | 1115 | 1 | Sqm | 8920
|  |  |  | Delifting Charges(Over intial -4M) | 41 | 1 | Cum | 41
|  |  |  | Municipal allowance | 20% |  |  | 356.8
|  |  |  | Overheads & cp |  | 13.61% |  | 1268.6185
[7 empty] | Total | 19295.7
|  | Ph.Side Wall | 100 | mm thick |  |  |  | Canal
|  | 1 | Cum | Cost of CC (1:1.5:3) | 8709.3 | 1 | Cum | 8709.3
|  | 10 | Sqm | Centering charges | 1115 | 1 | Sqm | 11150
|  |  |  | Municipal allowance | 20% |  |  | 557.5
|  |  |  | Overheads & cp |  | 13.61% |  | 1593.9761
[7 empty] | Total | 22010.8
| 42 | RCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for collection wellFloor Slab | [5 empty] | initial lift 3mts
|  |  | 150 | mm thick |  |  |  | Canal
|  | 1.5 | Cum | Cost of CC (1:1.5:3) | 6885.5 | 1 | Cum | 10328.25
|  | 6.6667 | Sqm | Centering charges | 389 | 1 | Sqm | 2593.3333
|  |  |  | Municipal allowance | 20% |  |  | 129.6667
|  |  |  | Overheads & cp |  | 13.61% |  | 370.7364
[7 empty] | Total 10sqmt | 13422
VRCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for ring beam -Gfloor Level Works
|  | 1 | Cum | Cost of CC (1:1.5:3) | 6885.5 | 1 | Cum | 6885.5
|  | 1 | Cum | Centering charges | 3428 | 1 | Cum | 3428
|  |  |  | Municipal allowance | 20% |  |  | 171.4
|  |  |  | Overheads & cp |  | 13.61% |  | 490.0583
[7 empty] | Total | 10975
| 43 | RCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for pump house top slab
|  |  | 100 | mm thick |  |  |  | Canal
|  | 1 | Cum | Cost of CC (1:1.5:3) | 6820.2 | 1 | Cum | 6820.2
|  | 10 | Sqm | Centering charges | 389 | 1 | Sqm | 3890
|  | 1 |  | Add lifting charges | 134 | 1 | Cum | 134
|  |  |  | Municipal allowance | 20% |  |  | 201.2
|  |  |  | Overheads & cp |  | 13.61% |  | 575.261
[7 empty] | Total 10sqmt | 11620.7
Intake Well-SSTank
|  | Intake-SSTank | 200 | mm thick |  |  |  | SSTank
|  | 1 | Cum | Cost of CC (1:1.5:3) | 8709.3 | 1 | Cum | 8709.3
|  | 5 | Sqm | Centering charges | 1115 | 1 | Sqm | 5575
|  |  |  | Municipal allowance | 20% |  |  | 223
|  |  |  | Overheads & cp |  | 13.61% |  | 789.3977
[7 empty] | Total | 15296.7
|  |  | 125 | mm thick |  |  |  | SSTank
|  | 1 | Cum | Cost of CC (1:1.5:3) | 8709.3 | 1 | Cum | 8709.3
|  | 8 | Sqm | Centering charges | 1115 | 1 | Sqm | 8920
|  |  |  | Lifting Charges(Over intial -5M) | 134 | 1 | Cum | 134
|  |  |  | Municipal allowance | 20% |  |  | 356.8
|  |  |  | Overheads & cp |  | 13.61% |  | 1281.2804
[7 empty] | Total | 19401.4
|  | Ph.Side Wall | 100 | mm thick |  |  |  | SSTank
|  | 1 | Cum | Cost of CC (1:1.5:3) | 8709.3 | 1 | Cum | 8709.3
|  | 10 | Sqm | Centering charges | 1115 | 1 | Sqm | 11150
|  |  |  | Municipal allowance | 20% |  |  | 557.5
|  |  |  | Overheads & cp |  | 13.61% |  | 1593.9761
[7 empty] | Total | 22010.8
RCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for collection wellFloor Slab
|  |  | 200 | mm thick |  |  |  | Canal
|  | 2 | Cum | Cost of CC (1:1.5:3) | 6820.2 | 1 | Cum | 13640.4
|  | 5 | Sqm | Centering charges | 418 | 1 | Sqm | 2090
|  |  |  | Municipal allowance | 20% |  |  | 104.5
|  |  |  | Overheads & cp |  | 13.61% |  | 298.7812
[7 empty] | Total 10sqmt | 16133.7
RCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for pump house top slab
|  |  | 100 | mm thick |  |  |  | Canal
|  | 1 | Cum | Cost of CC (1:1.5:3) | 6820.2 | 1 | Cum | 6820.2
|  | 10 | Sqm | Centering charges | 389 | 1 | Sqm | 3890
|  | 1 |  | Add lifting charges | 134 | 1 | Cum | 134
|  |  |  | Municipal allowance | 20% |  |  | 201.2
|  |  |  | Overheads & cp |  | 13.61% |  | 575.261
[7 empty] | Total 10sqmt | 11620.7
| 40 | VRCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for ring beam -Gfloor Level Works
|  | Sump |  |  | 0.3 | 0.3
|  | 1 | Cum | Cost of CC (1:1.5:3) | 8304.7 | 1 | Cum | 8304.7
|  | 1 | Cum | Centering charges | 3428 | 1 | Cum | 3428 | P-75 of Buildings
|  |  |  | Municipal allowance | 20% |  |  | 171.4
|  |  |  | Overheads & cp |  | 13.61% |  | 490.0583
[7 empty] | Total | 12394.2
| 41 | RCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for Columns
mm thick
|  | 1 | Cum | Cost of CC (1:1.5:3) | 8709.3 | 1 | Cum | 8709.3
|  | 1 | Cum | Centering charges | 2041 | 1 | Cum | 2041
|  |  |  | Municipal allowance | 20% |  |  | 102.05
|  |  |  | Overheads & cp | 13.61% |  |  | 291.7763
[7 empty] | Total | 11144.1
| 44 | VRCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for top dome
|  | Sump-Doome | 100 | mm thick
|  | 1 | Cum | Cost of CC (1:1.5:3) | 6885.5 | 1 | Cum | 6885.5
|  | 10 | sqm | Centering charges | 2670 | 1 | sqm | 26700
|  |  |  | Municipal allowance | 20% |  |  | 1335
|  |  |  | Overheads & cp |  | 13.61% |  | 3816.9652
[7 empty] | Total | 38737.5
|  | Sump-Doome | 150 | mm thick
|  | 1 | Cum | Cost of CC (1:1.5:3) | 6885.5 | 1 | Cum | 6885.5
|  | 6.6667 | sqm | Centering charges | 2670 | 1 | sqm | 17800
|  |  |  | Municipal allowance | 20% |  |  | 890
|  |  |  | Overheads & cp |  | 13.61% |  | 2544.6435
[7 empty] | Total | 28120.1
Sump Rectangle
VRCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for side wall of (St)
|  | Sump | 200 | mm thick
|  | 1 | Cum | Cost of CC (1:1.5:3) | 8709.3 | 1 | Cum | 8709.3
|  | 5 | Sqm | Centering charges | 876 | 1 | Sqm | 4380
|  |  |  | Municipal allowance | 20% |  |  | 219
|  |  |  | Overheads & cp |  | 13.61% |  | 626.1538
[7 empty] | Total | 13934.5
VRCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for side wall of (St)
|  | Sump | 150 | mm thick
|  | 1 | Cum | Cost of CC (1:1.5:3) | 8709.3 | 1 | Cum | 8709.3
|  | 6.6667 | Sqm | Centering charges | 876 | 1 | Sqm | 5840
|  |  |  | Municipal allowance | 20% |  |  | 292
|  |  |  | Overheads & cp |  | 13.61% |  | 834.8718
[7 empty] | Total | 15676.2
| 42 | Acco proof Plastering with CM (1:3) 12mm thick including cost and conveyance of all material, labour charges etc., complete
|  | 0.15 | Cum | Cost of CM(1:3) | 4863.2 | 1 | Cum | 729.48
|  | 0.6 | Nos. | Mason | 420 |  | Each | 252
|  | 0.96 | Nos. | Man Mazdoor | 320 |  | Each | 307.2
|  | 1.5 | Kg | Acco proof powder | 75 | 1 | Kg | 112.5
|  |  |  | Municipal allowance | 20% |  |  | 111.84
|  |  |  | Overheads & cp |  | 13.61% |  | 106.679
[7 empty] | Total | 1619.7
| 43 | Plastering with CM (1:3) 12mm thick including cost and conveyance of all material, labour charges etc., complete
|  | 0.15 | Cum | Cost of CM(1:3) | 4863.2 | 1 | Cum | 729.48
|  | 0.6 | Nos. | Mason | 420 |  | Each | 252
|  | 0.96 | Nos. | Man Mazdoor | 320 |  | Each | 307.2
|  |  |  | Municipal allowance | 20% |  |  | 111.84
|  |  |  | Overheads & cp |  | 13.61% |  | 91.3621
[7 empty] | Total | 1491.9
| 48 | Painting Walls with Snowcem or other equal and approved Water Proof Cement Paint over Priming Coat, 2 Coats (All Colours)
|  | 3.5 | Kg | Snowcem paint | 53 | 1 | KG | 185.5
|  | 0.5 | Nos. | Painters | 480 |  | Each | 240
|  | 1.5 | Nos. | Man mazdoor | 320 |  | Each | 480
|  |  |  | Sundries including brushes, etc., |  |  |  | 9.055
|  |  |  | Municipal allowance | 20% |  |  | 144
|  |  |  | Overheads & cp |  | 13.61% |  | 144.1223
[7 empty] | Total | 1202.7
Valve Chambers
| 44 | Cement concrete (1:4:8)prop using 40 mm gauge HG metal including cost &conveyance of all materials and labour charges ,seigniorage charges etc complete Hand Mixing
|  | 162 | Kgs | Cost of Cement | 6400 | 1 MT |  | 1036.8
|  | 0.9 | cum | Intial rate of 40mm metal @ | 1581.2583 | /cum |  | 1423.1324
|  | 0.45 | cum | Cost of Sand | 1010.7366 | /cum |  | 454.8315
|  | 1.2 | Kl | Water | 77 | Kl |  | 92.4
|  | 0.1 | Kl | Masons 1st class@ | 420 | /each |  | 42
|  | 2.36 | No | Mazdoor | 320 | /each |  | 755.2
|  |  |  | Municipal allowance | 20% |  |  | 159.44
|  |  |  | Overheads & cp |  | 13.61% |  | 539.6719
[7 empty] | Total Rs. | 4503.5
| 45 | VRCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for side wall of (Circular)
|  | Chambers | 100 | mm thick
|  | 1 | Cum | Cost of CC (1:1.5:3) | 8136.6 | 1 | Cum | 8136.6
|  | 10 | Sqm | Centering charges | 1115 | 1 | Sqm | 11150
|  |  |  | Municipal allowance | 20% |  |  | 557.5
|  |  |  | Overheads & cp |  | 13.61% |  | 1593.9761
[7 empty] | Total | 21438.1
| 46 | VRCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for side wall of (straight)
|  | Chambers | 100 | mm thick
|  | 1 | Cum | Cost of CC (1:1.5:3) | 8136.6 | 1 | Cum | 8136.6
|  | 10 | Sqm | Centering charges | 876 | 1 | Sqm | 8760
|  |  |  | Municipal allowance | 20% |  |  | 438
|  |  |  | Overheads & cp |  | 13.61% |  | 1252.3077
[7 empty] | Total | 18586.9
|  | Chambers | 200 | mm thick
|  | 1 | Cum | Cost of CC (1:1.5:3) | 8136.6 | 1 | Cum | 8136.6
|  | 5 | Sqm | Centering charges | 876 | 1 | Sqm | 4380
|  |  |  | Municipal allowance | 20% |  |  | 219
|  |  |  | Overheads & cp |  | 13.61% |  | 626.1538
[7 empty] | Total | 13361.8
| 47 | VRCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for slab of Chambers
|  |  | 100 | mm thick
|  | 1 | Cum | Cost of VRCC (1:1.5:3) | 6820.2 | 1 | Sqm | 6820.2
|  | 1 | Cum | Centering charges | 389 | 1 | Cum | 389
|  |  |  | Municipal allowance | 20% |  |  | 19.45
|  |  |  | Overheads & cp |  | 13.61% |  | 55.6105
Sundies
[7 empty] | Total | 7284.3
Collection Well with Girders
VRCC(1:1.5:3) using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for Raft ring Beam
excluding cost of steel
[5 empty] | 1.65 | 0.4
|  | 1 | Cum | cost of RCC(1:11/2:3) | 8304.7 | 1 | Cum | 8304.7
|  | 1.2121 | Sqm | Centering charges | 3428 | 1 | Cum | 4155.1515
|  | 1 |  | Delifting Charges | 41 |  |  | 41
|  |  |  | Municipal allowance | 20% |  |  | 209.8076
|  |  |  | Overheads & cp |  | 13.61% |  | 599.9
[7 empty] | Total | 13310.5591
VRCC(1:1.5:3) using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for Side Wall (upto 3mts below and 3mts above GL)
0.45
|  | 1 | Cum | Cost of CC (1:1.5:3) | 8709.3 | 1 | Cum | 8709.3
|  | 2.2222 | Sqm | Centering charges | 1115 | 1 | Sqm | 2477.7778 |  | 16.67%
|  |  |  | Municipal allowance | 20% |  |  | 123.8889
|  |  |  | Overheads & cp | 13.61% |  |  | 354.2169 |  |  |  | Calculation of Centering & Scaffolding charges for every 0.61mts height at the rate of 16.666%
|  |  | - | 0 - 3 Mts |  |  | Total | 11665.1836
[6 empty] | centering & scaffolding | [5 empty] | 3 | 0.61
[5 empty] | per 1m lift |  | lift charges |  |  | multiple |  | 3.61 | 1
|  | Lifting | 1 | 3 - 4 Mts | 134 | 2917.68 | 153.1563 | 14736.0199 |  | 1 | 3.61 | 4.22 | 2 | 0.16666 | 185.8259 | 2891.1111 | 2917.68
|  |  | 3 | 4 - 5 Mts |  | 1751.7 | 153.1563 | 13570.0399 |  | 3 | 4.83 | 4.83 | 3 | 0.49998 | 557.4777 | 1672 | 1751.7
|  |  | 4 | 5 - 6 Mts |  | 1964.26 | 153.1563 | 13782.5999 |  | 4 | 5.44 | 5.44 | 4 | 0.66664 | 743.3036 | 1858 | 1964.26
|  |  | 5 | 6-7 Mts |  | 2176.83 | 153.1563 | 13995.1699 |  | 5 | 6.66 | 6.05 | 5 | 0.8333 | 929.1295 | 2044 | 2176.83
|  |  | 7 | 7-8 Mts |  | 2601.96 | 153.1563 | 14420.2999 |  | 7 | 7.88 | 6.66 | 6 | 1.1666 | 1300.7813 | 2416 | 2601.96
|  |  | 8 | 8-9mts |  | 2814.52 | 153.1563 | 14632.8599 |  | 8 | 8.49 | 7.27 | 7 | 1.3333 | 1486.6072 | 2602 | 2814.52
|  |  | 11 | 9-10mts |  | 3451.22 | 153.1563 | 15269.5599 |  | 11 | 9.71 | 7.88 | 8 | 1.8333 | 2044.0849 | 3159 | 3451.22
|  |  | 13 | 10-11mts |  | 3876.35 | 153.1563 | 15694.6899 |  | 13 | 10.93 | 8.49 | 9 | 2.1666 | 2415.7367 | 3531 | 3876.35
|  |  | 14 | 11-12mts |  | 4088.91 | 153.1563 | 15907.2499 |  | 14 | 11.54 | 9.1 | 10 | 2.3332 | 2601.5626 | 3717 | 4088.91
|  |  | 16 | 12-13mts |  | 4513.04 | 153.1563 | 16331.3799 |  | 16 | 12.76 | 9.71 | 11 | 2.6666 | 2973.2144 | 4088 | 4513.04
|  |  | 18 | 13-14mts |  | 4938.17 | 153.1563 | 16756.5099 |  | 18 | 13.98 | 10.32 | 12 | 2.9999 | 3344.8662 | 4460 | 4938.17
|  |  | 19 | 14-15mts |  | 5150.74 | 153.1563 | 16969.0799 |  | 19 | 14.59 | 10.93 | 13 | 3.1665 | 3530.6921 | 4646 | 5150.74
|  |  | 21 | 15-16mts |  | 5574.87 | 153.1563 | 17393.2099 |  | 21 | 15.81 | 11.54 | 14 | 3.4999 | 3902.3439 | 5017 | 5574.87
|  |  | 22 | 16-17mts |  | 5787.43 | 153.1563 | 17605.7699 |  | 22 | 16.42 | 12.15 | 15 | 3.6665 | 4088.1698 | 5203 | 5787.43
|  |  | 24 | 17-18mts |  | 6212.56 | 153.1563 | 18030.8999 |  | 24 | 17.64 | 12.76 | 16 | 3.9998 | 4459.8216 | 5575 | 6212.56
|  |  | 26 | 18-19mts |  | 6636.7 | 153.1563 | 18455.0399 |  | 26 | 18.86 | 13.37 | 17 | 4.3332 | 4831.4734 | 5946 | 6636.7
|  |  | 27 | 19-20mts |  | 6849.26 | 153.1563 | 18667.5999 |  | 27 | 19.47 | 13.98 | 18 | 4.4998 | 5017.2993 | 6132 | 6849.26
|  |  | 29 | 20-21mts |  | 7274.39 | 153.1563 | 19092.7299 |  | 29 | 20.69 | 14.59 | 19 | 4.8331 | 5388.9511 | 6504 | 7274.39
|  |  | 31 | 21-22mts |  | 7699.52 | 153.1563 | 19517.8599 |  | 31 | 21.91 | 15.2 | 20 | 5.1665 | 5760.6029 | 6876 | 7699.52
|  |  | 32 | 22-23mts |  | 7911.09 | 153.1563 | 19729.4299 |  | 32 | 22.52 | 15.81 | 21 | 5.3331 | 5946.4288 | 7061 | 7911.09
|  |  | 34 | 23-24mts |  | 8336.22 | 153.1563 | 20154.5599 |  | 34 | 23.74 | 16.42 | 22 | 5.6664 | 6318.0806 | 7433 | 8336.22
|  |  | 36 | 24-25mts |  | 8761.35 | 153.1563 | 20579.6899 |  | 36 | 24.96 | 17.03 | 23 | 5.9998 | 6689.7324 | 7805 | 8761.35
[12 empty] | 17.64 | 24
|  | VRCC(1:1.5:3) using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for Side Wall | [9 empty] | 18.25 | 25
[5 empty] | 0.4 | [6 empty] | 18.86 | 26
|  | 1 | Cum | Cost of CC (1:1.5:3) | 8709.3 | 1 | Cum | 8709.3 |  |  |  | 19.47 | 27
|  | 2.5 | Sqm | Centering charges | 1115 | 1 | Sqm | 2787.5 |  |  |  | 20.08 | 28
|  |  |  | Municipal allowance | 20% |  |  | 139.375 |  |  |  | 20.69 | 29
|  |  |  | Overheads & cp | 13.61% |  |  | 398.494 |  |  |  | 21.3 | 30
|  |  | - | 0 - 3 Mts |  |  | Total | 12034.669 |  |  |  | 21.91 | 31
|  |  | 1 | 3 -4 Mts |  | 3277.8 | 153.1563 | 15465.6253 | 3691.2162 |  |  | 22.52 | 32
|  |  | 3 | 4 - 5 Mts |  | 1747.9 | 153.1563 | 13935.7253 |  |  |  | 23.13 | 33
|  |  | 4 | 5 - 6 Mts |  | 1959.2 | 153.1563 | 14147.0253 |  |  |  | 23.74 | 34
|  |  | 5 | 6-7 Mts |  | 2170.5 | 153.1563 | 14358.3253 |  |  |  | 24.35 | 35
|  |  | 7 | 7-8 Mts |  | 2593.1 | 153.1563 | 14780.9253 |  |  |  | 24.96 | 36
|  |  | 8 | 8-9mts |  | 2804.4 | 153.1563 | 14992.2253
|  |  | 11 | 9-10mts |  | 3437.3 | 153.1563 | 15625.1253
|  |  | 13 | 10-11mts |  | 3859.9 | 153.1563 | 16047.7253
|  |  | 14 | 11-12mts |  | 4071.2 | 153.1563 | 16259.0253
|  |  | 16 | 12-13mts |  | 4492.8 | 153.1563 | 16680.6253
|  |  | 18 | 13-14mts |  | 4915.4 | 153.1563 | 17103.2253
|  |  | 19 | 14-15mts |  | 5126.7 | 153.1563 | 17314.5253
|  |  | 21 | 15-16mts |  | 5548.3 | 153.1563 | 17736.1253
|  |  | 22 | 16-17mts |  | 5759.6 | 153.1563 | 17947.4253
|  |  | 24 | 17-18mts |  | 6182.2 | 153.1563 | 18370.0253
|  |  | 26 | 18-19mts |  | 6603.81 | 153.1563 | 18791.6353
|  |  | 27 | 19-20mts |  | 6815.11 | 153.1563 | 19002.9353
|  |  | 29 | 20-21mts |  | 7237.71 | 153.1563 | 19425.5353
|  |  | 31 | 21-22mts |  | 7660.31 | 153.1563 | 19848.1353
|  |  | 32 | 22-23mts |  | 7870.61 | 153.1563 | 20058.4353
|  |  | 34 | 23-24mts |  | 8293.21 | 153.1563 | 20481.0353
|  |  | 36 | 24-25mts |  | 8715.81 | 153.1563 | 20903.6353
VRCC(1:1.5:3) using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for Side Wall
0.35
|  | 1 | Cum | Intial rate |  |  |  | 8709.3
|  | 2.8571 | Sqm | side wall cetering charges | 1115 |  |  | 3185.7143
|  |  |  | Municipal allowance | 20% |  |  | 159.2857
|  |  |  | Overheads & cp | 13.61% |  |  | 455.4217
|  |  |  | 0-3mts |  |  |  | 12509.7217
|  | Lifting |  | 3 - 4 Mts | 134 | 3742.44 | 153.1563 | 16405.3181
|  |  |  | 4 - 5 Mts |  | 1747.9 | 153.1563 | 14410.7781
|  |  |  | 5 - 6 Mts |  | 1959.2 | 153.1563 | 14622.0781
|  |  |  | 6-7 Mts |  | 2170.5 | 153.1563 | 14833.3781
|  |  |  | 7-8 Mts |  | 2593.1 | 153.1563 | 15255.9781
|  |  |  | 8-9mts |  | 2804.4 | 153.1563 | 15467.2781
|  |  |  | 9-10mts |  | 3437.3 | 153.1563 | 16100.1781
|  |  |  | 10-11mts |  | 3859.9 | 153.1563 | 16522.7781
|  |  |  | 11-12mts |  | 4071.2 | 153.1563 | 16734.0781
|  |  |  | 12-13mts |  | 4492.8 | 153.1563 | 17155.6781
|  |  |  | 13-14mts |  | 4915.4 | 153.1563 | 17578.2781
|  |  |  | 14-15mts |  | 5126.7 | 153.1563 | 17789.5781
|  |  |  | 15-16mts |  | 5548.3 | 153.1563 | 18211.1781
|  |  |  | 16-17mts |  | 5759.6 | 153.1563 | 18422.4781
|  |  |  | 17-18mts |  | 6182.2 | 153.1563 | 18845.0781
|  |  |  | 18-19mts |  | 6603.81 | 153.1563 | 19266.6881
|  |  |  | 19-20mts |  | 6815.11 | 153.1563 | 19477.9881
|  |  |  | 20-21mts |  | 7237.71 | 153.1563 | 19900.5881
|  |  |  | 21-22mts |  | 7660.31 | 153.1563 | 20323.1881
|  |  |  | 22-23mts |  | 7870.61 | 153.1563 | 20533.4881
|  |  |  | 23-24mts |  | 8293.21 | 153.1563 | 20956.0881
|  |  |  | 24-25mts |  | 8715.81 | 153.1563 | 21378.6881
VRCC(1:1.5:3) using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for Side Wall
0.3
|  | 1 | Cum | Intial rate |  |  |  | 8709.3
|  | 3.3333 | Sqm | side wall cetering charges | 1115 |  |  | 3716.6667
|  |  |  | Municipal allowance | 20% |  |  | 185.8333
|  |  |  | Overheads & cp | 13.61% |  |  | 531.3254
|  |  |  | 0-3mts |  |  |  | 13143.1254
|  | Lifting |  | 3 - 4 Mts | 134 | 4361.97 | 153.1563 | 17024.8481
|  |  |  | 4 - 5 Mts |  | 1747.9 | 153.1563 | 14410.7781
|  |  |  | 5 - 6 Mts |  | 1959.2 | 153.1563 | 14622.0781
|  |  |  | 6-7 Mts |  | 2170.5 | 153.1563 | 14833.3781
|  |  |  | 7-8 Mts |  | 2593.1 | 153.1563 | 15255.9781
|  |  |  | 8-9mts |  | 2804.4 | 153.1563 | 15467.2781
|  |  |  | 9-10mts |  | 3437.3 | 153.1563 | 16100.1781
|  |  |  | 10-11mts |  | 3859.9 | 153.1563 | 16522.7781
|  |  |  | 11-12mts |  | 4071.2 | 153.1563 | 16734.0781
|  |  |  | 12-13mts |  | 4492.8 | 153.1563 | 17155.6781
|  |  |  | 13-14mts |  | 4915.4 | 153.1563 | 17578.2781
|  |  |  | 14-15mts |  | 5126.7 | 153.1563 | 17789.5781
|  |  |  | 15-16mts |  | 5548.3 | 153.1563 | 18211.1781
|  |  |  | 16-17mts |  | 5759.6 | 153.1563 | 18422.4781
|  |  |  | 17-18mts |  | 6182.2 | 153.1563 | 18845.0781
|  |  |  | 18-19mts |  | 6603.81 | 153.1563 | 19266.6881
|  |  |  | 19-20mts |  | 6815.11 | 153.1563 | 19477.9881
|  |  |  | 20-21mts |  | 7237.71 | 153.1563 | 19900.5881
|  |  |  | 21-22mts |  | 7660.31 | 153.1563 | 20323.1881
|  |  |  | 22-23mts |  | 7870.61 | 153.1563 | 20533.4881
|  |  |  | 23-24mts |  | 8293.21 | 153.1563 | 20956.0881
|  |  |  | 24-25mts |  | 8715.81 | 153.1563 | 21378.6881
VRCC(1:1.5:3) using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for Side Wall
0.25
|  | 1 | Cum | Intial rate |  |  |  | 8709.3
|  | 4 | Sqm | side wall cetering charges | 1115 |  |  | 4460
|  |  |  | Municipal allowance | 20% |  |  | 223
|  |  |  | Overheads & cp | 13.61% |  |  | 637.5904
|  |  |  | 0-3mts |  |  |  | 14029.8904
|  | Lifting |  | 3 - 4 Mts | 134 | 5229.3 | 153.1563 | 17892.1781
|  |  |  | 4 - 5 Mts |  | 1747.9 | 153.1563 | 14410.7781
|  |  |  | 5 - 6 Mts |  | 1959.2 | 153.1563 | 14622.0781
|  |  |  | 6-7 Mts |  | 2170.5 | 153.1563 | 14833.3781
|  |  |  | 7-8 Mts |  | 2593.1 | 153.1563 | 15255.9781
|  |  |  | 8-9mts |  | 2804.4 | 153.1563 | 15467.2781
|  |  |  | 9-10mts |  | 3437.3 | 153.1563 | 16100.1781
|  |  |  | 10-11mts |  | 3859.9 | 153.1563 | 16522.7781
|  |  |  | 11-12mts |  | 4071.2 | 153.1563 | 16734.0781
|  |  |  | 12-13mts |  | 4492.8 | 153.1563 | 17155.6781
|  |  |  | 13-14mts |  | 4915.4 | 153.1563 | 17578.2781
|  |  |  | 14-15mts |  | 5126.7 | 153.1563 | 17789.5781
|  |  |  | 15-16mts |  | 5548.3 | 153.1563 | 18211.1781
|  |  |  | 16-17mts |  | 5759.6 | 153.1563 | 18422.4781
|  |  |  | 17-18mts |  | 6182.2 | 153.1563 | 18845.0781
|  |  |  | 18-19mts |  | 6603.81 | 153.1563 | 19266.6881
|  |  |  | 19-20mts |  | 6815.11 | 153.1563 | 19477.9881
|  |  |  | 20-21mts |  | 7237.71 | 153.1563 | 19900.5881
|  |  |  | 21-22mts |  | 7660.31 | 153.1563 | 20323.1881
|  |  |  | 22-23mts |  | 7870.61 | 153.1563 | 20533.4881
|  |  |  | 23-24mts |  | 8293.21 | 153.1563 | 20956.0881
|  |  |  | 24-25mts |  | 8715.81 | 153.1563 | 21378.6881
VRCC(1:1.5:3) using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for Side Wall
0.2
|  | 1 | Cum | Intial rate |  |  |  | 8709.3
|  | 5 | Sqm | side wall cetering charges | 1115 |  |  | 5575
|  |  |  | Municipal allowance | 20% |  |  | 278.75
|  |  |  | Overheads & cp | 13.61% |  |  | 796.9881
|  |  |  | 0-3mts |  |  |  | 15360.0381
|  | Lifting |  | 3 - 4 Mts | 134 | 6530.3 | 153.1563 | 19193.1781
|  |  |  | 4 - 5 Mts |  | 1747.9 | 153.1563 | 14410.7781
|  |  |  | 5 - 6 Mts |  | 1959.2 | 153.1563 | 14622.0781
|  |  |  | 6-7 Mts |  | 2170.5 | 153.1563 | 14833.3781
|  |  |  | 7-8 Mts |  | 2593.1 | 153.1563 | 15255.9781
|  |  |  | 8-9mts |  | 2804.4 | 153.1563 | 15467.2781
|  |  |  | 9-10mts |  | 3437.3 | 153.1563 | 16100.1781
|  |  |  | 10-11mts |  | 3859.9 | 153.1563 | 16522.7781
|  |  |  | 11-12mts |  | 4071.2 | 153.1563 | 16734.0781
|  |  |  | 12-13mts |  | 4492.8 | 153.1563 | 17155.6781
|  |  |  | 13-14mts |  | 4915.4 | 153.1563 | 17578.2781
|  |  |  | 14-15mts |  | 5126.7 | 153.1563 | 17789.5781
|  |  |  | 15-16mts |  | 5548.3 | 153.1563 | 18211.1781
|  |  |  | 16-17mts |  | 5759.6 | 153.1563 | 18422.4781
|  |  |  | 17-18mts |  | 6182.2 | 153.1563 | 18845.0781
|  |  |  | 18-19mts |  | 6603.81 | 153.1563 | 19266.6881
|  |  |  | 19-20mts |  | 6815.11 | 153.1563 | 19477.9881
|  |  |  | 20-21mts |  | 7237.71 | 153.1563 | 19900.5881
|  |  |  | 21-22mts |  | 7660.31 | 153.1563 | 20323.1881
|  |  |  | 22-23mts |  | 7870.61 | 153.1563 | 20533.4881
|  |  |  | 23-24mts |  | 8293.21 | 153.1563 | 20956.0881
|  |  |  | 24-25mts |  | 8715.81 | 153.1563 | 21378.6881
VRCC(1:1.5:3) using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for Side Wall
0.15
|  | 1 | Cum | Intial rate |  |  |  | 8709.3
|  | 6.6667 | Sqm | side wall cetering charges | 1115 |  |  | 7433.3333
|  |  |  | Municipal allowance | 20% |  |  | 371.6667
|  |  |  | Overheads & cp | 13.61% |  |  | 1062.6508
|  |  |  | 0-3mts |  |  |  | 17576.9507
|  | Lifting |  | 3 - 4 Mts | 134 | 8698.63 | 153.1563 | 21361.5081
|  |  |  | 4 - 5 Mts |  | 1747.9 | 153.1563 | 14410.7781
|  |  |  | 5 - 6 Mts |  | 1959.2 | 153.1563 | 14622.0781
|  |  |  | 6-7 Mts |  | 2170.5 | 153.1563 | 14833.3781
|  |  |  | 7-8 Mts |  | 2593.1 | 153.1563 | 15255.9781
|  |  |  | 8-9mts |  | 2804.4 | 153.1563 | 15467.2781
|  |  |  | 9-10mts |  | 3437.3 | 153.1563 | 16100.1781
|  |  |  | 10-11mts |  | 3859.9 | 153.1563 | 16522.7781
|  |  |  | 11-12mts |  | 4071.2 | 153.1563 | 16734.0781
|  |  |  | 12-13mts |  | 4492.8 | 153.1563 | 17155.6781
|  |  |  | 13-14mts |  | 4915.4 | 153.1563 | 17578.2781
|  |  |  | 14-15mts |  | 5126.7 | 153.1563 | 17789.5781
|  |  |  | 15-16mts |  | 5548.3 | 153.1563 | 18211.1781
|  |  |  | 16-17mts |  | 5759.6 | 153.1563 | 18422.4781
|  |  |  | 17-18mts |  | 6182.2 | 153.1563 | 18845.0781
|  |  |  | 18-19mts |  | 6603.81 | 153.1563 | 19266.6881
|  |  |  | 19-20mts |  | 6815.11 | 153.1563 | 19477.9881
|  |  |  | 20-21mts |  | 7237.71 | 153.1563 | 19900.5881
|  |  |  | 21-22mts |  | 7660.31 | 153.1563 | 20323.1881
|  |  |  | 22-23mts |  | 7870.61 | 153.1563 | 20533.4881
|  |  |  | 23-24mts |  | 8293.21 | 153.1563 | 20956.0881
|  |  |  | 24-25mts |  | 8715.81 | 153.1563 | 21378.6881
|  | VRCC(1:1.5:3) using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for Side Wall | [6 empty] | Not updated
0.275
|  | 1 | Cum | Intial rate |  |  |  | 8709.3
|  | 3.6364 | Sqm | side wall cetering charges | 1115 |  |  | 4054.5455
|  | 6 |  | Lift charges | 134 |  |  | 804
|  |  |  | Municipal allowance | 20% |  |  | 202.7273
|  |  |  | Overheads & cp | 13.61% |  |  | 689.0923
|  |  |  | 20-23mt | 134 |  | Total | 14459.665
|  |  |  | 20-23mt | (Lift Charges) | 14593.665 | 19.1563 | 14612.8213
|  | VRCC(1:1.5:3) using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for Pump House Side Wall | [6 empty] | Not updated
0.15
|  | 1 | Cum | Intial rate |  |  |  | 8136.6
|  | 6.6667 | Sqm | side wall cetering charges | 1115 |  |  | 7433.3333
|  | 8 |  | Lift charges | 134 |  |  | 1072
|  |  |  | Municipal allowance | 20% |  |  | 371.6667
|  |  |  | Overheads & cp | 13.61% |  |  | 1208.6036
|  |  |  | 20-23mt | 134 |  | Total | 18222.2036
|  |  |  | 20-23mt | (Lift Charges) | 18356.2036 | 19.1563 | 18375.3599
|  | RCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for pump house top slab | [6 empty] | Not updated
|  |  | 150 | mm thick
|  | 1.5 | Cum | Cost of CC (1:1.5:3) | 6820.2 | 1 | Cum | 10230.3
|  | 6.6667 | Sqm | Centering charges | 389 | 1 | Sqm | 2593.3333
|  | 18 |  | Add lifting charges | 134 | 1 | Cum | 2412
|  |  |  | Municipal allowance | 20% |  |  | 250.2667
|  |  |  | Overheads & cp | 13.61% |  |  | 715.5499
[7 empty] | Total 10sqmt | 16201.4
RCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for Floor Slab
|  |  | 200 | mm thick |  |  |  |  | Not updated
|  | 2 | Cum | Cost of CC (1:1.5:3) | 6820.2 | 1 | Cum | 13640.4
|  | 5 | Sqm | Centering charges | 418 | 1 | Sqm | 2090
|  | 13 |  | Add lifting charges | 134 | 1 | Cum | 1742
|  |  |  | Municipal allowance | 20% |  |  | 191.6
|  |  |  | Overheads & cp | 13.61% |  |  | 547.8131
[7 empty] | Total 10sqmt | 18211.8
| 53 | VRCC (1:1.5:3) using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for ring beam | [6 empty] | Not updated
|  | 1 | Cum | Cost of CC (1:1.5:3) | 8304.7 | 1 | Cum | 8304.7
|  | 1 | Cum | Centering charges | 3428 | 1 | Cum | 3428 | P-75 of Buildings
|  | 17 | lift | Add lifting charges | 134 | 1 | Cum | 2278
|  |  |  | Municipal allowance | 20% |  |  | 171.4
|  |  |  | Overheads & cp |  | 13.61% |  | 800.208
[7 empty] | Total | 14982.3
|  |  |  | OHBR (M30 Design Mix) | Column type
M 30 Grade concrete using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for OHBR Ring Beam
[5 empty] | 0.15 | 0.5
|  | 1 | Cum | cost of RCC(1:11/2:3) | 8304.7 | 1 | Cum | 8304.7
|  | 4 | Sqm | Centering charges | 1206 | 1 | Cum | 4824
|  |  |  | extra allowance on centring charges | 27% |  |  | 1302.5
|  |  |  | Municipal allowance | 20% |  |  | 306.325
|  |  |  | Overheads & cp |  | 13.61% |  | 875.8
[7 empty] | Total | 15613.3
M 30 Grade concrete using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for Columns
[5 empty] | 0.45 | 0.45
|  | 1 | Cum | Intial rate |  |  |  | 8709.3
|  | 8.9 | Sqm | coulmn cetering charges | 1099 | 1 Sq mt |  | 9781.1
|  |  |  | extra allowance on centring charges | 27% |  |  | 2640.897
|  |  |  | Municipal allowance | 20% |  |  | 621.0999
|  |  |  | Overheads & cp | 13.61% |  |  | 1775.8
|  |  |  | 0 - 3 Mts |  |  | Total | 23528.1969
|  | 1 | lifts | 3 - 4 Mts | 134 | 23662.1969 | 19.1563 | 23681.3532
|  | 1 | lifts | 4 - 5 Mts | (Lift Charges) | 23815.3532 | 19.1563 | 23834.5095
|  | 1 | lifts | 5 - 6 Mts |  | 23968.5095 | 19.1563 | 23987.6658
|  | 1 | lifts | 6-7 Mts |  | 24121.6658 | 19.1563 | 24140.8221
|  | 1 | lifts | 7-8 Mts |  | 24274.8221 | 19.1563 | 24293.9784
|  | 1 | lifts | 8-9 Mts |  | 24427.9784 | 19.1563 | 24447.1347
|  | 1 | lifts | 9-10 Mts |  | 24581.1347 | 19.1563 | 24600.291
|  | 1 | lifts | 10-11 Mts |  | 24734.291 | 19.1563 | 24753.4473
|  | 1 | lifts | 11-12 Mts |  | 24887.4473 | 19.1563 | 24906.6036
|  | 1 | lifts | 12-13mts |  | 25040.6036 | 19.1563 | 25059.7599
|  | 1 | lifts | 13-14mts |  | 25193.7599 | 19.1563 | 25212.9162
|  | 1 | lifts | 14-15mts |  | 25346.9162 | 19.1563 | 25366.0725
|  | 1 | lifts | 15-16mts |  | 25500.0725 | 19.1563 | 25519.2288
|  | 1 | lifts | 16-17mts |  | 25653.2288 | 19.1563 | 25672.3851
|  | 1 | lifts | 17-18mts |  | 25806.3851 | 19.1563 | 25825.5414
|  | 1 | lifts | 18-19mts |  | 25959.5414 | 19.1563 | 25978.6977
|  | 1 | lifts | 19-20mts |  | 26112.6977 | 19.1563 | 26131.854
|  | 1 | lifts | 20-21mts |  | 26265.854 | 19.1563 | 26285.0103
|  | 1 | lifts | 21-22mts |  | 26419.0103 | 19.1563 | 26438.1666
|  | 1 | lifts | 22-23mts |  | 26572.1666 | 19.1563 | 26591.323
|  | 1 | lifts | 23-24mts |  | 26725.323 | 19.1563 | 26744.4793
|  | 1 | lifts | 24-25mts |  | 26878.4793 | 19.1563 | 26897.6356
|  | 1 | lifts | 25-26mts |  | 27031.6356 | 19.1563 | 27050.7919
M 30 grade concrete using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for Braces
[5 empty] | 0.55 | 0.4
|  | 1 | Cum | Intial rate |  |  |  | 8709.3
|  | 6.8182 | Sqm | Brace cetering charges | 1099 | 1 Sq mt |  | 7493.1818
|  |  |  | extra allowance on centring charges | 27% |  |  | 2023.1591
|  |  |  | Municipal allowance | 20% |  |  | 475.817
|  |  |  | Overheads & cp | 13.61% |  |  | 1360.4323
|  |  |  | 0 - 5 Mts |  |  | Total | 20061.8903
|  | 3 | lifts | 5 - 8 Mts | 402 | 20463.8903 | 57.4689 | 20521.3592
|  | 3 | lifts | 8 - 11 Mts | (Lift Charges) | 20923.3592 | 57.4689 | 20980.8281
|  | 3 | lifts | 11- 14 Mts |  | 21382.8281 | 57.4689 | 21440.297
|  | 3 | lifts | 14- 17 Mts |  | 21842.297 | 57.4689 | 21899.7659
|  | 3 | lifts | 17- 20 Mts |  | 22301.7659 | 57.4689 | 22359.2348
|  | 3 | lifts | 20- 23Mts |  | 22761.2348 | 57.4689 | 22818.7038
M 30 Grade concrete using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for Tank bottom ring beam
[5 empty] | 0.55 | 0.4
|  | 1 | Cum | Intial rate |  |  |  | 6885.5
|  | 6.8182 | Sqm | centering charges | 1206 |  |  | 8222.7273
|  | 22 |  | Lift charges | 134 |  |  | 2948
|  |  |  | extra allowance on centring charges | 27% |  |  | 2220.1364
|  |  |  | Municipal allowance | 20% |  |  | 522.1432
|  |  |  | Overheads & cp |  | 13.61% |  | 1894.2559
[7 empty] | Total | 22692.8
M 30 Grade concrete using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for Tank ring beam
[5 empty] | 0.2 | 0.15
|  | 1 | Cum | Intial Rate |  |  |  | 6885.5
|  | 18.3333 | Sqm | centering charges | 1206 | 1 Sq mt |  | 22110
|  | 25 |  | Lift charges | 134 |  |  | 3350
|  |  |  | extra allowance on centring charges | 27% |  |  | 5969.7
|  |  |  | Municipal allowance | 20% |  |  | 1403.985
|  |  |  | Overheads & cp |  | 13.61% |  | 4470.3062
[7 empty] | Total | 44189.5
M 30 Grade concrete using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for Side Wall
0.1
|  | 1 | Cum | Intial Rate |  |  |  | 8709.3
|  | 10 | Sqm | side wall cetering charges | 2463 |  |  | 24630
|  | 24 |  | Lift charges | 134 |  |  | 3216
|  |  |  | extra allowance on centring charges | 27% |  |  | 6650.1
|  |  |  | Municipal allowance | 20% |  |  | 1564.005
|  |  |  | Overheads & cp |  | 13.61% |  | 4909.5833
[7 empty] | Total | 49679
M 30 grade concrete using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for OHBR Top slab Dome
0.075
|  | 1 | Cum | Intial Rate |  |  |  | 6885.5
|  | 13.3333 | Sqm | cetering charges | 2670 |  |  | 35600
|  | 25 |  | Lift charges | 134 |  |  | 3350
|  |  |  | extra allowance on centring charges | 27% |  |  | 720.9
|  |  |  | Municipal allowance | 20% |  |  | 169.545
|  |  |  | Overheads & cp |  | 13.61% |  | 5424.2766
[7 empty] | Total | 52150.2
M 30 grade concrete using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for OHBR bottom Dome
0.125
|  | 1 | Cum | Intial Rate |  |  |  | 6885.5
|  | 8 | Sqm | cetering charges | 2670 |  |  | 21360
|  | 22 |  | Lift charges | 134 |  |  | 2948
|  |  |  | extra allowance on centring charges | 27% |  |  | 720.9
|  |  |  | Municipal allowance | 20% |  |  | 169.545
|  |  |  | Overheads & cp |  | 13.61% |  | 3430.7683
[7 empty] | Total | 35514.7
Shaft Type OHBR
M 30 grade concrete using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for shaft side wall
|  |  | 0.3 | M
|  | 1 | Cum | Intial Rate |  |  |  | 8709.3
|  | 3.3333 | Sqm | side wall cetering charges | 2463 |  |  | 8210
|  | 0 |  | Lift charges | 134 |  |  | 0
|  |  |  | extra allowance on centring charges | 30% |  |  | 2463
|  |  |  | Municipal allowance | 20% |  |  | 533.65
|  |  |  | Overheads & cp | 13.61% |  |  | 1525.7854
[7 empty] | Total | 21441.7
|  |  | 0.25 | M
|  | 1 | Cum | Intial Rate |  |  |  | 8709.3
|  | 4 | Sqm | side wall cetering charges | 2463 |  |  | 9852
|  | 0 |  | Lift charges | 134 |  |  | 0
|  |  |  | extra allowance on centring charges | 30% |  |  | 2955.6
|  |  |  | Municipal allowance | 20% |  |  | 640.38
|  |  |  | Overheads & cp | 13.61% |  |  | 1830.9425
[7 empty] | Total | 23988.2
M 30 grade concrete using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for Tank ring beam
[5 empty] | 0.3 | 0.3
|  | 1 | Cum | Intial Rate |  |  |  | 6885.5
|  | 10 | Sqm | centering charges | 1206 | 1 Sq mt |  | 12060
|  | 0 |  | Lift charges | 134 |  |  | 0
|  |  |  | extra allowance on centring charges | 30% |  |  | 3618
|  |  |  | Municipal allowance | 20% |  |  | 783.9
|  |  |  | Overheads & cp |  | 13.61% |  | 2241.2877
[7 empty] | Total | 25588.7
M 30 grade concrete using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for shaft side wall
0.2
|  | 1 | Cum | Intial Rate |  |  |  | 8709.3
|  | 5 | Sqm | side wall cetering charges | 2463 |  |  | 12315
|  | 0 |  | Lift charges | 134 |  |  | 0
|  |  |  | extra allowance on centring charges | 30% |  |  | 3694.5
|  |  |  | Municipal allowance | 20% |  |  | 800.475
|  |  |  | Overheads & cp | 13.61% |  |  | 2288.6781
|  |  |  | 0 - 3 Mts |  |  | Total | 27808
|  |  |  | 3 - 4 Mts | lift charges | 134 | 27942 | 27960.2
|  |  |  | 4 - 5 Mts |  |  | 28094.2 | 28112.4
|  |  |  | 5 - 6 Mts |  |  | 28246.4 | 28264.6
|  |  |  | 6-7 Mts |  |  | 28398.6 | 28416.8
|  |  |  | 7-8 Mts |  |  | 28550.8 | 28569
|  |  |  | 8-9 Mts |  |  | 28703 | 28721.2
|  |  |  | 9-10 Mts |  |  | 28855.2 | 28873.4
|  |  |  | 10-11 Mts |  |  | 29007.4 | 29025.6
|  |  |  | 11-12 Mts |  |  | 29159.6 | 29177.8
|  |  |  | 12-13mts |  |  | 29311.8 | 29330
|  |  |  | 13-14mts |  |  | 29464 | 29482.2
|  |  |  | 14-15mts |  |  | 29616.2 | 29634.4
|  |  |  | 15-16mts |  |  | 29768.4 | 29786.6
|  |  |  | 16-17mts |  |  | 29920.6 | 29938.8
|  |  |  | 17-18mts |  |  | 30072.8 | 30091
|  |  |  | 18-19mts |  |  | 30225 | 30243.2
|  |  |  | 19-20mts |  |  | 30377.2 | 30395.4
|  |  |  | 20-21mts |  |  | 30529.4 | 30547.6
|  |  |  | 21-22mts |  |  | 30681.6 | 30699.8
|  |  |  | 22-23mts |  |  | 30833.8 | 30852
|  |  |  | 23-24mts |  |  | 30986 | 31004.2
|  |  |  | 24-25mts |  |  | 31138.2 | 31156.4
|  |  |  | 25-26mts |  |  | 31290.4 | 31308.6
|  |  |  | 26-27mts |  |  | 31442.6 | 31460.8
|  |  |  | 27-28mts |  |  | 31594.8 | 31613
|  |  |  | 28-29mts |  |  | 31747 | 31765.2
|  |  |  | 29-30mts |  |  | 31899.2 | 31917.4
M 30 grade concrete using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for Tank bottom slab
0.3
|  | 1 | Cum | Intial Rate |  |  |  | 6885.5
|  | 3.3333 | Sqm | cetering charges | 2670 |  |  | 8900
|  | 27 |  | Lift charges | 134 |  |  | 3618
|  |  |  | extra allowance on centring charges | 30% |  |  | 2670
|  |  |  | Municipal allowance | 20% |  |  | 578.5
|  |  |  | Overheads & cp |  | 13.61% |  | 2146.609
[7 empty] | Total | 24798.6
M 30 grade concrete using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for Tank Top slab
0.15
|  | 1 | Cum | Intial Rate |  |  |  | 6885.5
|  | 6.6667 | Sqm | cetering charges | 2670 |  |  | 17800
|  | 32 |  | Lift charges | 134 |  |  | 4288
|  |  |  | extra allowance on centring charges | 30% |  |  | 5340
|  |  |  | Municipal allowance | 20% |  |  | 1157
|  |  |  | Overheads & cp |  | 13.61% |  | 3891.8477
[7 empty] | Total | 39362.3
M 30 grade concrete using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for Tank ring beam
[5 empty] | 0.3 | 0.4
|  | 1 | Cum | Intial Rate |  |  |  | 6885.5
|  | 8.3333 | Sqm | centering charges | 1206 | 1 Sq mt |  | 10050
|  | 27 |  | Lift charges | 134 |  |  | 3618
|  |  |  | extra allowance on centring charges | 30% |  |  | 3015
|  |  |  | Municipal allowance | 20% |  |  | 653.25
|  |  |  | Overheads & cp |  | 13.61% |  | 2360.3304
[7 empty] | Total | 26582.1
M 30 grade concrete using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for Conical Side Wall
0.2
|  | 1 | Cum | Intial Rate |  |  |  | 8709.3
|  | 5 | Sqm | side wall cetering charges | 2463 |  |  | 12315
|  | 30 |  | Lift charges | 134 |  |  | 4020
|  | (Average) |  | extra allowance on centring charges | 30% |  |  | 3694.5
|  |  |  | Municipal allowance | 20% |  |  | 800.475
|  |  |  | Overheads & cp |  | 13.61% |  | 2836.0011
[7 empty] | Total | 32375.3
M 30 grade concrete using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for Tank ring beam
[5 empty] | 0.3 | 0.4
|  | 1 | Cum | Intial Rate |  |  |  | 6885.5
|  | 8.3333 | Sqm | centering charges | 1206 | 1 Sq mt |  | 10050
|  | 33 |  | Lift charges | 134 |  |  | 4422
|  |  |  | extra allowance on centring charges | 30% |  |  | 3015
|  |  |  | Municipal allowance | 20% |  |  | 653.25
|  |  |  | Overheads & cp |  | 13.61% |  | 2469.795
[7 empty] | Total | 27495.5
M 30 grade concrete using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for inner shaft side Wall
0.15
|  | 1 | Cum | Intial Rate |  |  |  | 8709.3
|  | 6.6667 | Sqm | side wall cetering charges | 2463 |  |  | 16420
|  | 30 |  | Lift charges | 134 |  |  | 4020
|  |  |  | extra allowance on centring charges | 30% |  |  | 4926
|  |  |  | Municipal allowance | 20% |  |  | 1067.3
|  |  |  | Overheads & cp |  | 13.61% |  | 3598.8938
[7 empty] | Total | 38741.5
M 30 grade concrete using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for inner shaft Flat slab
0.15
|  | 1 | Cum | Intial Rate |  |  |  | 6885.5
|  | 6.6667 | Sqm | Slab cetering charges | 6302 |  |  | 42013.3333
|  | 29 |  | Lift charges | 134 |  |  | 3886
|  |  |  | extra allowance on centring charges | 30% |  |  | 12604
|  |  |  | Municipal allowance | 20% |  |  | 2730.8667
|  |  |  | Overheads & cp |  | 13.61% |  | 8337.0363
[7 empty] | Total | 76456.7
M 30 grade concrete using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for Tank top dome
0.125
|  | 1 | Cum | Intial Rate |  |  |  | 6885.5
|  | 8 | Sqm | cetering charges | 2670 |  |  | 21360
|  | 33 |  | Lift charges | 134 |  |  | 4422
|  |  |  | extra allowance on centring charges | 30% |  |  | 6408
|  |  |  | Municipal allowance | 20% |  |  | 1388.4
|  |  |  | Overheads & cp |  | 13.61% |  | 4571.6992
[7 empty] | Total | 45035.6
M 30 grade concrete using 20 mm HBG metal including cost,conveyance and labour etc.. Complete for Landing slab
0.125
|  | 1 | Cum | Intial Rate |  |  |  | 6885.5
|  | 8 | Sqm | Slab cetering charges | 6302 |  |  | 50416
|  | 0 |  | Lift charges | 134 |  |  | 0
|  |  |  | extra allowance on centring charges | 30% |  |  | 15124.8
|  |  |  | Municipal allowance | 20% |  |  | 3277.04
|  |  |  | Overheads & cp |  | 13.61% |  | 9369.5489
|  |  |  | 0 - 5 Mts |  |  | Total | 85072.8889
|  |  |  | 5 - 8 Mts | lift charges | 402 | 85474.8889 | 85493.133
|  |  |  | 8 - 11 Mts |  |  | 85895.133 | 85913.3771
|  |  |  | 11 - 14 Mts |  |  | 86315.3771 | 86333.6212
|  |  |  | 14-17 Mts |  |  | 86735.6212 | 86753.8653
|  |  |  | 17-20 Mts |  |  | 87155.8653 | 87174.1094
|  |  |  | 20-23 Mts |  |  | 87576.1094 | 87594.3535
|  |  |  | 23-26 Mts |  |  | 87996.3535 | 88014.5976
|  |  |  | 26-29 Mts |  |  | 88416.5976 | 88434.8417
|  |  |  | 29-32 Mts |  |  | 88836.8417 | 88855.0858
|  |  |  | For stair case columns | 30 | m staging
M 30 grade concrete using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for Column(Circular)
[5 empty] | Column | 0.4 | Circular
|  | 1 | cum | Intial Rate |  |  |  | 8709.3
|  | 10 | Sqm | coulmn cetering charges | 1206 |  |  | 12060
|  |  |  | extra allowance on centring charges | 30% |  |  | 3618
|  |  |  | Municipal allowance | 20% |  |  | 783.9
|  |  |  | Overheads & cp |  | 13.61% |  | 2241.2877
|  |  |  | 0 - 3 Mts |  |  | Total | 27412.4877
|  |  |  | 3 - 4 Mts | lift charges | 134 | 27546.4877 | 27564.7318
|  |  |  | 4 - 5 Mts |  |  | 27698.7318 | 27716.9759
|  |  |  | 5 - 6 Mts |  |  | 27850.9759 | 27869.22
|  |  |  | 6-7 Mts |  |  | 28003.22 | 28021.4641
|  |  |  | 7-8 Mts |  |  | 28155.4641 | 28173.7082
|  |  |  | 8-9 Mts |  |  | 28307.7082 | 28325.9523
|  |  |  | 9-10 Mts |  |  | 28459.9523 | 28478.1964
|  |  |  | 10-11 Mts |  |  | 28612.1964 | 28630.4405
|  |  |  | 11-12 Mts |  |  | 28764.4405 | 28782.6846
|  |  |  | 12-13mts |  |  | 28916.6846 | 28934.9287
|  |  |  | 13-14mts |  |  | 29068.9287 | 29087.1728
|  |  |  | 14-15mts |  |  | 29221.1728 | 29239.4169
|  |  |  | 15-16mts |  |  | 29373.4169 | 29391.661
|  |  |  | 16-17mts |  |  | 29525.661 | 29543.9051
|  |  |  | 17-18mts |  |  | 29677.9051 | 29696.1492
|  |  |  | 18-19mts |  |  | 29830.1492 | 29848.3933
|  |  |  | 19-20mts |  |  | 29982.3933 | 30000.6374
|  |  |  | 20-21mts |  |  | 30134.6374 | 30152.8815
|  |  |  | 21-22mts |  |  | 30286.8815 | 30305.1256
|  |  |  | 22-23mts |  |  | 30439.1256 | 30457.3697
|  |  |  | 23-24mts |  |  | 30591.3697 | 30609.6138
|  |  |  | 24-25mts |  |  | 30743.6138 | 30761.8579
|  |  |  | 25-26mts |  |  | 30895.8579 | 30914.102
|  |  |  | 26-27mts |  |  | 31048.102 | 31066.3461
|  |  |  | 27-28mts |  |  | 31200.3461 | 31218.5902
|  |  |  | 28-29mts |  |  | 31352.5902 | 31370.8343
|  |  |  | 29-30mts |  |  | 31504.8343 | 31523.0784
|  |  |  | 30 -31mts |  |  | 31657.0784 | 31675.3225
|  |  |  | 31 - 32mts |  |  | 31809.3225 | 31827.5666
|  |  |  | 32 -33mts |  |  | 31961.5666 | 31979.8107
M 30 grade concrete using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for steps treads-50mm thick
0.05
|  | 1 | cum | Intial rate |  |  |  | 6885.5
|  | 20 | 1Cum | coulmn cetering charges | 480 |  |  | 9600
|  |  |  | extra allowance on centring charges | 30% |  |  | 2880
|  |  |  | Municipal allowance | 20% |  |  | 624
|  |  |  | Overheads & cp |  | 13.61% |  | 1784.1096
|  |  |  | 0 - 5 Mts | 0 lifts |  | Total | 21773.6096
|  |  |  | 5 - 8 Mts | lift charges | 402 | 22175.6096 | 22230.3419
|  |  |  | 8 - 11 Mts |  |  | 22632.3419 | 22687.0742
|  |  |  | 11 - 14 Mts |  |  | 23089.0742 | 23143.8065
|  |  |  | 14-17 Mts |  |  | 23545.8065 | 23600.5388
|  |  |  | 17-20 Mts |  |  | 24002.5388 | 24057.2711
|  |  |  | 20-23 Mts |  |  | 24459.2711 | 24514.0034
|  |  |  | 23-26 Mts |  |  | 24916.0034 | 24970.7357
|  |  |  | 26-29 Mts |  |  | 25372.7357 | 25427.468
|  |  |  | 29-32 Mts |  |  | 25829.468 | 25884.2003
|  |  |  | 32-32.4 Mts |  |  | 26286.2003 | 26340.9326
M 30 grade concrete using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for steps Risers-50mm thick
0.05
|  | 1 | Cum | Intial Rate |  |  |  | 6885.5
|  | 20 | 1Cum | coulmn cetering charges |  | 480 | 1 Sq mt | 9600
|  |  |  | extra allowance on centring charges |  | 30% |  | 2880
|  |  |  | Municipal allowance | 0.2 |  |  | 624
|  |  |  | Overheads & cp | 13.61% |  |  | 1784.1096
|  |  |  | 0 - 5 Mts |  |  | Total | 21773.6096
|  |  |  | 5 - 8 Mts | lift charges | 402 | 22175.6096 | 25194.8188
|  |  |  | 8 - 11 Mts |  |  | 22577.6096 | 25651.5511
|  |  |  | 11 - 14 Mts |  |  | 22979.6096 | 26108.2834
|  |  |  | 14-17 Mts |  |  | 23381.6096 | 26565.0157
|  |  |  | 17-20 Mts |  |  | 23783.6096 | 27021.748
|  |  |  | 20-23 Mts |  |  | 24185.6096 | 27478.4803
|  |  |  | 23-26 Mts |  |  | 24587.6096 | 27935.2126
|  |  |  | 26-29 Mts |  |  | 24989.6096 | 28391.9449
|  |  |  | 29-32 Mts |  |  | 25391.6096 | 28848.6772
|  |  |  | 32-32.4 Mts |  |  | 25793.6096 | 29305.4095
M 30 grade concrete using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for Tie Brace
[5 empty] | 0.3 | 0.3
|  | 1 | Cum | Intial Rate |  |  | 1 Cum | 6885.5
|  | 10 | Sqm | Brace cetering charges |  | 1206 | 1 Sq mt | 12060
|  |  |  | extra allowance on centring charges |  | 30% |  | 3618
|  |  |  | Municipal allowance | 0.2 |  |  | 783.9
|  |  |  | Overheads & cp | 13.61% | 0% |  | 2241.2877
Sundries
|  |  |  | 0 - 5 Mts | 0 lifts |  | Total | 25588.7
|  |  |  | 5 - 8 Mts | lift charges | 402 | 25990.7 | 26045.4323
|  |  |  | 8 - 11 Mts |  |  | 26447.4323 | 26502.1646
|  |  |  | 11- 14 Mts |  |  | 26904.1646 | 26958.8969
|  |  |  | 14- 17 Mts |  |  | 27360.8969 | 27415.6292
|  |  |  | 17- 20 Mts |  |  | 27817.6292 | 27872.3615
|  |  |  | 20- 23 Mts |  |  | 28274.3615 | 28329.0938
|  |  |  | 23- 26 Mts |  |  | 28731.0938 | 28785.8261
|  |  |  | 26- 29 Mts |  |  | 29187.8261 | 29242.5584
|  |  |  | 29- 32 Mts |  |  | 29644.5584 | 29699.2907
M 30 grade concrete using 20mm HBG metal including cost and conveyance of all material, labour charges, centering etc., complete but excluding cost of steel and its fabrication charges for Top flat slab
|  |  |  | Intial rate | 0.1 | 6820.2 | 0.125 | 6820.2
|  | 10 | 8 | cetering charges | 6302 | 63020 |  | 50416
|  | 29 |  | Lift charges | 134 | 3886 |  | 3886
|  |  |  | extra allowance on centring charges | 30% | 18906 | 30% | 15124.8
|  |  |  | Municipal allowance | 20% | 4096.3 |  | 3277.04
|  |  |  | Overheads & cp | 13.61% | 12241.015 |  | 3963.0596
[6 empty] | 108969.5 |  | 83487.1
SSTank
| Stripping | IRR-CAW-1-1 | Excavation in all kinds of soil including boulders upto 0.3 m diameter for canal, seating of
embankment, filter drains / catch water drains etc., including dressing bed and sides to
required level and profile, cost of all materials, machinery, labour, placing the excavated soil
neatly in dump area or for the formation of service road / embankment as directed etc.,
complete with initial lead upto 1 km and all lifts.
|  | DATA: | Capacity of shovel bucket |  |  | : | 0.85 | cum
|  |  | Capacity of shovel bucket under heaped condition |  |  | : | 1 | cum
|  |  | Capacity of tipper |  |  | : | 5 | cum
|  |  | Lead for disposal of excavated soil |  |  | :Upto | 1 | km
|  |  | Speed for loaded tipper under canal excavation condition |  |  | : | 15 | km / hr | 0.066667
|  |  | Speed for empty tipper under canal excavation condition |  |  | : | 15 | km / hr
|  |  | Turning and unloading time |  |  | : | 2 | min
|  |  | Shovel digging and loading cycle per bucket |  |  | : | 20 | sec
|  |  | In-situ quantity / bucket for 20 % bulkage on unloading ( 1 /1.20 ) |  |  | : | 0.83 | cum
|  |  | In-situ quantity per load for 20 % bulkage of soil ( 5 /1.2 ) |  |  | : | 4.16 | cum
|  |  | Number of buckets per load ( 4.16 / 0.83 ) |  |  | say : | 5 | buckets
|  |  | Corrected Quantity of in-situ soil per load ( 5 x 0.83 ) |  |  | say : | 4.16 | cum
|  |  | Ideal cycle time for loading 5 buckets ( 5 x 20 / 60 ) |  |  | : | 1.67 | min
The ideal cycle time for shovel requires spotting of a tipper within 1.67 minutes near the shovel.
However, in practice for canal excavation the space available may not permit positioning of the
tippers on either side of the shovel. Generally, one tipper has to move after loading to position
the next tipper for loading. Assuming one cycle time extra the corrected cycle time for the
shovel will be 2.00 minutes.
floor trip cycle time for tipper:
|  |  | Ideal cycle time of shovel for digging & loading |  |  | : | 1.67 | min
|  |  | Time for ( av ) 0.75km haulage under load ( 0.75 x 60 / 15 ) |  |  | : | 3 | min
|  |  | Time for turning and un-loading |  |  | : | 2 | min
|  |  | Time for average 0.75 km return trip ( 0.75 x 60 / 15 ) |  |  | : | 3 | min
|  |  | Extra time for spotting |  |  | : | 0.33 | min
|  |  | Total time |  |  | : | 10 | min
|  |  | No. of tippers to match corrected cycle time of shovel ( 10.00/ 2.00 ) |  |  | : | 5 | Nos
|  |  | Output of tipper / hr with 50 min working / hr ( 50 x 4.16 / 10.00 ) |  |  | : | 20.8 | cum
|  |  | Output for 5 tippers per day ( 5 x 20.80 x 8 ) |  |  | : | 832 | cum
Further, assuming about 90 percent of excavation by deploying shovel and about 10 percent
excavation mainly for trimming the canal to final profile by manual labour the daily output will
|  |  | be : |  |  | say : | 925 | cum
Average output of 2 mazdoors assumed at 6 cum / day for trimming.
Deploy 30 mazdoors for trimming 93 cum.
Deploy one tipper for disposal of manually excavated soil.
|  | DATA: |  | RATE ANALYSIS |  | UNIT : | 925 | cum
A. MATERIALS:
|  |  | Sl No | particulars | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | NIL |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
|  |  |  | Total cost of Materials |  |  | Rs: | 0
B. MACHINERY:
|  |  | Sl No | Description | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Shovel 0.85 cum capacity | Hour | 8 | 1706.6 | 13652.8
|  |  |  | Fuel / Energy charges | Hour | 8 | 862.1 | 6896.8
|  |  | 2 | Tippers 5 cum capacity 6 Nos | Hour | 48 | 446.7 | 21441.6
|  |  |  | Fuel / Energy charges | Hour | 48 | 296.3 | 14222.4
|  |  |  | Total hire charges of Machinery |  |  | Rs: | 56213.6
C. LABOUR:
|  |  | Sl No | Description | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Crew for Shovel | Hour | 8 | 222.3 | 1778.4
|  |  | 2 | Crew for Tipper | Hour | 48 | 166.7 | 8001.6
|  |  | 3 | work inspector | Day | 1 | 400 | 400
|  |  | 4 | mazdoor | Day | 30 | 320 | 9600
|  |  |  | Total cost of Labour |  |  | Rs: | 19780
|  |  | labour component/unit qty |  |  | 21.3838
|  |  | Overheads & cp |  | 13.61% | 2.9114
|  |  | labour component/unit qty (including Overheads & cp) |  |  | 24.2952
ABSTRACT:
|  |  | A. Cost of Materials |  |  |  | Rs: | 0
|  |  | B. Hire charges of Machinery |  |  |  | Rs: | 56213.6
|  |  | C. Cost of Labour |  |  |  | Rs: | 19780 | (Add MA if necessary))
|  |  |  | Municipal allowance | 20% |  |  | 3956
|  |  | Total |  |  |  | Rs: | 79949.6
|  |  | D. Add for Overheads & cp on (A+B+C) |  |  | 13.61% | Rs: | 10885.138
|  |  | Total cost for |  | 925 | cum | Rs: | 90834.738
|  |  | Rate per | cum | (A+B+C+D)/925 |  | Rs. | 98.2
SS Tank
| only consolidation for key trench | IRR-CAW-4-1 | Providing impervious hearting embankment with soil collected in embankment area in
heaps as part of disposal of excavated soil from canal including cost of all materials,machinery,
labour, all operations such as sortingout, spreading in layer of 25 cm before compaction,
breaking clods,sectioning, watering and compacting each layer to density control of not less
than 98 percent or as stipulated by sheep's foot / pad foot roller etc., complete with lead upto
1 km for water.
|  | DATA: | Quantity of embankment considered |  |  |  | : | 600
|  | 1 | Stripping of borrow area :
No stripping of top soil involved as useful soil from excavation is collected.
|  | 2 | Collection of soil for embankment:
Soil already collected in embankment area as part of disposal of excavated soil
from canal excavation.
|  | 3 | Spreading soil in 25 cm layer:
|  |  | Quantity of loose soil to be spread ( 600 x 1.20 ) |  |  |  | : | 720
|  |  | Output of dozer for levelling per hour |  |  |  | : | 200
|  |  | Time required for levelling 720 cum |  |  |  | say : | 3.6
|  | 4 | Watering;
Generally soil from canal excavation will be in moist condition.In the beginning of the season no
watering may be necessary and in summer months about 8 to 10 percent watering may be
needed to maintain the soil moisture within OMC plus or minus 3 percent limit. Assuming
seasonal average of 4 to 5 percent watering by weight, daily requirement of water for 600 cum
of embankment will be about 5 tanker loads of 8000 ltrs each.
Deploy 8000 ltr capacity water tanker for 5 hours daily for watering before rolling.
Deploy 5 hp pump for 3 hours.
|  | 5 | Compaction:
Soil collected for embankment layer gets compacted to some extent during levelling.
Generally 10 to 12 passes of vibratory pad foot roller is adequate for achieving specified density
control of 98 percent.
|  |  | Effective length of roller drum |  |  |  | : | 1.9
|  |  | Speed of roller per hour |  |  |  | : | 4
|  |  | Thickness of layer |  |  |  | : | 0.25
|  |  | Number of roller passes to achieve specified density control |  |  |  | : | 12
Output of roller / hr with 50 min /hr working and 75 % effenciancy
|  |  | 50 / 60 ( 1.9 x 4000 x 0.25 x 0.75 / 12 ) |  |  |  | say : | 99
|  |  | Time for rolling 720 cum soil in embankment layer |  |  | 7.2727 | say : | 7.3
|  | 6 | Sorting out/ sectioning/ labour for testing etc :
Assume 4 mazdoors.
|  | DATA: |  | RATE ANALYSIS |  | UNIT : | 600 | cum
A. MATERIALS:
|  |  | Sl No | particulars | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Nill |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
|  |  |  | Seioniorage charges for soil | cum |  | 19.3636 | 11618.1842
|  |  |  | Total cost of Materials |  |  | Rs: | 11618.1842
B. MACHINERY:
|  |  | Sl No | Description | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Angle dozer 90 hp | Hour | 3.6 | 1715.5 | 6175.8
|  |  |  | Fuel / Energy charges | Hour | 3.6 | 603.1 | 2171.16
|  |  | 2 | Pump 5 hp ( diesel ) | Hour | 3 | 10.2 | 30.6
|  |  |  | Fuel / Energy charges | Hour | 3 | 78.4 | 235.2
|  |  | 3 | Water tanker 8000 ltr | Hour | 5 | 402.5 | 2012.5
|  |  |  | Fuel / Energy charges | Hour | 5 | 296.3 | 1481.5
|  |  | 4 | Vibratory pad foot roller 8 tonne | Hour | 7.3 | 1342.2 | 9798.06
|  |  |  | Fuel / Energy charges | Hour | 7.3 | 1018.9 | 7437.97
|  |  | 5 | Sundries | LS | 2 | 41 | 82
|  |  |  | Total hire charges of Machinery |  |  | Rs: | 29424.79
C. LABOUR:
|  |  | Sl No | Description | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Crew for Dozer | Hour | 3.6 | 222.3 | 800.28
|  |  | 2 | Crew for Pump | Hour | 3 | 104.8 | 314.4
|  |  | 3 | Crew for Water tanker | Hour | 5 | 166.7 | 833.5
|  |  | 4 | Crew for Roller | Hour | 7.3 | 248 | 1810.4
|  |  | 5 | work inspector | Day | 1 | 400 | 400
|  |  | 6 | mazdoor | Day | 4 | 320 | 1280
|  |  |  | Total cost of Labour |  |  | Rs: | 5438.58
|  |  | labour component/unit qty |  |  | 9.0643
|  |  | Overheads & cp |  | 13.61% | 1.2341
|  |  | labour component/unit qty (including Overheads & cp) |  |  | 5.4075
ABSTRACT:
|  |  | A. Cost of Materials including seignorage charges |  |  |  | Rs: | 11618.1842
|  |  | B. Hire charges of Machinery |  |  |  | Rs: | 29424.79
|  |  | C. Cost of Labour |  |  |  | Rs: | 5438.58 | (Add MA if necessary))
|  |  |  | Municipal allowance | 20% |  |  | 1087.716
[7 empty] | Total Rs: | 47569.2702
|  |  | D. Add for Overheads & cp on (A+B+C) |  |  | 13.61% | Rs: | 6476.5561
|  |  | Total cost for |  | 600 | cum | Rs: | 54045.8264
|  |  | Rate per | cum | (A+B+C+D)/600 |  | Rs. | 90.1
|  | IRR-CAW-1-2 | Excavation in all kinds of soil including boulders upto 0.30 m dia for field channels, seating
| EW for key trench & Toe wall |  | of embankment for field channels etc., including dressing of bed and sides to required profile,
cost of all materials, machinery, labour, placing the excavated stuff for formation of service
road / embankment as directed etc., complete with lead upto 10 m and lift upto 3 m.
|  | DATA: | Capacity of shovel bucket |  |  | : | 0.5 | cum
|  |  | Capacity of shovel bucket under heaped condition |  |  | : | 0.57 | cum
|  |  | Lead for disposal of excavated soil |  |  | :Upto | 10 | m
|  |  | Shovel digging and loading cycle per bucket |  |  | : | 30 | sec
|  |  | In-situ qty / bucket for 15 % bulkage of soil ( 0.57 / 1.15 ) |  |  | : | 0.5 | cum
|  |  | Output of shovel with 50 min./ hr working ( 50 x 60 x 0.5 / 30 ) |  |  | : | 50 | cum / hr
|  |  | Daily output of excavation ( 8 x 50 ) |  |  | : | 400 | cum
Further, assuming about 90 percent of excavation by deploying shovel and about 10 percent
excavation mainly for trimming bed and sides of channels / trenches to final profile by manual
|  |  | labour, the daily output will be : |  |  | say : | 440 | cum
|  | DATA: | Average output of 2 mazdoors assumed at 5 cum / day for trimming
|  |  |  | RATE ANALYSIS |  | UNIT : | 440 | cum
A. MATERIALS:
|  |  | Sl No | particulars | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | NIL |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
|  |  |  | Total cost of Materials |  |  | Rs: | 0
B. MACHINERY:
|  |  | Sl No | Description | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Shovel 0.50 cum capacity | Hour | 8 | 1003.1 | 8024.8
|  |  |  | Fuel / Energy charges | Hour | 8 | 470.3 | 3762.4
|  |  |  | Total hire charges of Machinery |  |  | Rs: | 11787.2
C. LABOUR:
|  |  | Sl No | Description | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Crew for Shovel | Hour | 8 | 222.3 | 1778.4
|  |  | 2 | work inspector | Day | 1 | 400 | 400
|  |  | 3 | mazdoor | Day | 17 | 320 | 5440
|  |  |  | Total cost of Labour |  |  | Rs: | 7618.4
|  |  | labour component/unit qty |  |  | 17.3145
|  |  | Add Overheads & cp and overhead charges |  | 13.61% | 2.3574
|  |  | labour component/unit qty (including Overheads & cp) |  |  | 19.6719
ABSTRACT:
|  |  | A. Cost of Materials |  |  |  | Rs: | 0
|  |  | B. Hire charges of Machinery |  |  |  | Rs: | 11787.2
|  |  | C. Cost of Labour |  |  |  | Rs: | 7618.4 | (Add MA if necessary))
|  |  |  | Municipal allowance | 20% |  |  | 1523.68
[7 empty] | Total Rs: | 20929.28
|  |  | D. Add for Overheads & cp on (A+B+C) |  |  | 13.61% | Rs: | 2849.5215
|  |  | Total cost for |  | 440 | cum | Rs: | 23778.8015
|  |  | Rate per | cum | (A+B+C+D)/440 |  | Rs. | 54
| Consolidation borrowed earth | IRR-CAW-2-6 | Providing hearting / casing embankment with homogeneous soil from approved borrow
areas in layers of 25 cm before compaction including cost of all materials, machinery,
labour, all operations such as excavation, sorting out, transporting, spreading in layer of
specified thickness, breaking clods, sectioning, watering, compacting each layer to density
control of not less than 98 percent or as stipulated by sheep / pad foot roller etc., complete
with initial lead upto 1 km and all lifts.
|  | DATA: | Capacity of shovel bucket |  |  |  | : | 0.5 | cum
|  |  | Capacity of shovel bucket under heaped condition |  |  |  | : | 0.58 | cum
|  |  | Capacity of tipper |  |  |  | : | 5 | cum
|  |  | Lead for conveyance of soil |  |  |  | :Upto | 5 | km
|  |  | Speed for loaded tipper under haul road condition |  |  |  | : | 12 | km / hr
|  |  | Speed for empty tipper under haul road condition |  |  |  | : | 15 | km / hr
|  |  | Turning and unloading time |  |  |  | : | 2 | min
|  |  | Shovel digging and loading cycle per bucket |  |  |  | : | 20 | sec
|  |  | In-situ qty / bucket for 15 % bulkage of soil ( 0.58 /1.15 ) |  |  |  | : | 0.5 | cum
|  |  | In-situ quantity per load for 20 % bulkage of soil ( 5.0 /1.2 ) |  |  |  | : | 4 | cum
|  |  | Number of buckets per load ( 4.00 / 0.50 ) |  |  |  | say : | 8 | buckets
|  |  | Cycle time for loading 8 buckets ( 8 x 20 / 60 ) |  |  |  | say : | 2.67 | min
|  |  | round trip cycle time for tipper: |  |  |  | :
|  |  | Ideal cycle time of shovel for digging & loading |  |  |  | : | 2.67 | min
|  |  | Time for 1km haulage under load ( 60 / 12 ) x 5 Km |  | 25 |  | : | 25 | min
|  |  | Time for turning and un-loading |  |  |  | : | 2 | min
|  |  | Time for 1 km return trip ( 60 / 15 ) x 5 Km |  | 20 |  | : | 20 | min
|  |  | Time for turning and spotting |  |  |  | : | 0.5 | min
[7 empty] | : | 50.17 | min
|  |  | No. of tippers to match corrected cycle time of shovel |  | 50.17 | 2.67 | 19 | 19 | Nos
|  |  | Output of tipper / hr with 50 min working / hr ( 50 x 4.00 / 50.17 ) : |  |  |  | 4 | 4 | cum
|  |  | Output for 19 tippers per day (19 x 4 x 8) |  | 608 |  | say : | 608 | cum
|  | 1 | Stripping of borrow area :
Generally borrow area is stripped once in a week for 6 days requirement of soil.
|  |  | Area to be stripped assuming 1.5 m depth of cut (608 x 19 / 1.5 ) : |  |  |  | 7701.3333 | 7701.3333 | sqm
|  |  | Depth of stripping |  |  |  | : | 0.2 | m
|  |  | Qty of stripping with 5 % extra area ( 7701.33333333333x1.05x0.2 ) |  |  |  | : | 1617.3 | cum
|  |  | Output of dozer per hr with 50 min / hr working for stripping |  |  |  | : | 70 | cum
|  |  | Time required for stripping 1617.3 cum |  |  |  | : | 23.1 | hours
Consider 6 hours including time for levelling stripped siol / shifting time.
|  |  | Requirement of dozer for one day work 705.6 cum |  |  |  | 3.85 | 2 | hours | say
|  | 2 | Collection of soil for embankment:
Deploy one 0.50 cum capacity shovel for 8 hours for digging and loading soil.
Deploy 4 tippers of 5.00 cum capacity for 8 hours to convey soil to embankment area.
|  | 3 | Spreading soil in 25 cm layer:
|  |  | Quantity of loose soil to be spread (608 x 1.2 ) : |  |  |  | : | 729.6 | cum
|  |  | Output of dozer for levelling per hour |  |  |  | : | 200 | cum
|  |  | Time required for levelling 812.74 cum |  |  | 3.648 | say : | 3.648 | hours
|  | 4 | Watering; |  |  |  |  | 3.65 | hours
Generally soil in the borrow area will be in moist condition. In the beginning of the season no
watering may be necessary and in summer months about 8 to 10 percent watering may be
needed to maintain the soil moisture within OMC plus or minus 3 percent limit. Assuming
seasonal average of 4 to 5 percent watering by weight, daily requirement of water for 677.28 cum
of embankment will be about 6 tanker loads of 8000 ltrs each. Deploy 8000 ltr capacity water
tanker for 6 hours daily for watering before rolling. Deploy 5 hp pump for 3 hours.
|  | 5 | Compaction:
Soil collected for embankment layer gets compacted to some extent during levelling.
Generally 10 to 12 passes of vibratory pad foot roller is adequate for achieving specified density
control of 98 percent.
|  |  | Effective length of roller drum |  |  |  | : | 1.9 | m
|  |  | Speed of roller per hour |  |  |  | : | 4 | km
|  |  | Thickness of layer |  |  |  | : | 0.25 | m
|  |  | Number of roller passes to achieve specified density control |  |  |  | : | 11 | Nos
Output of roller / hr with 50 min /hr working and 75 % effenciancy
|  |  | 50 / 60 ( 1.9 x 4000 x 0.25 x 0.75 /11 ) |  |  | 107.95 | say : | 107.95 | cum
|  |  | Time for rolling 812.74 cum soil in embankment layer |  |  |  | say : | 7.53 | hours
|  | 6 | Sorting out/ sectioning/ labour for testing etc :
Assume 4 mazdoors.
|  | DATA: |  | RATE ANALYSIS |  | UNIT : | 608 | cum
A. MATERIALS:
|  |  | Sl No | particulars | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Nill |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
|  |  |  | Seioniorage charges for soil | cum |  | 19.3636 | 11773.0933
|  |  |  | Total cost of Materials |  |  | Rs: | 11773.0933
B. MACHINERY:
|  |  | Sl No | Description | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Angle dozer | Hour | 5.65 | 1715.5 | 9692.575
|  |  |  | Fuel / Energy charges | Hour | 5.65 | 603.1 | 3407.515
|  |  | 2 | Shovel 0.50 cum capacity | Hour | 8 | 1003.1 | 8024.8
|  |  |  | Fuel / Energy charges | Hour | 8 | 470.3 | 3762.4
|  |  | 3 | Tippers 5.00 cum capacity 6 Nos. | Hour | 152 | 446.7 | 67898.4
|  |  |  | Fuel / Energy charges | Hour | 152 | 296.3 | 45037.6
|  |  | 4 | Pump 5 hp ( diesel ) | Hour | 3 | 10.2 | 30.6
|  |  |  | Fuel / Energy charges | Hour | 3 | 78.4 | 235.2
|  |  | 5 | Water tanker 8000 ltr | Hour | 6 | 402.5 | 2415
|  |  |  | Fuel / Energy charges | Hour | 6 | 296.3 | 1777.8
|  |  | 6 | Vibratory pad foot roller 8 tonne | Hour | 7.53 | 1342.2 | 10106.766
|  |  |  | Fuel / Energy charges | Hour | 7.53 | 1018.9 | 7672.317
|  |  | 7 | Sundries | LS | 2 | 41 | 82
|  |  |  | Total hire charges of Machinery |  |  | Rs: | 160142.973
C. LABOUR:
|  |  | Sl No | Description | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Crew for Dozer | Hour | 5.65 | 222.3 | 1255.995
|  |  | 2 | Crew for Shovel | Hour | 8 | 222.3 | 1778.4
|  |  | 3 | Crew for Tipper | Hour | 152 | 166.7 | 25338.4
|  |  | 4 | Crew for Pump | Hour | 3 | 104.8 | 314.4
|  |  | 5 | Crew for Water tanker | Hour | 6 | 166.7 | 1000.2
|  |  | 6 | Crew for Roller | Hour | 7.53 | 248 | 1867.44
|  |  | 7 | work inspector | Day | 2 | 400 | 800
|  |  | 8 | mazdoor | Day | 4 | 320 | 1280
|  |  |  | Total cost of Labour |  |  | Rs: | 33634.835
193777.808
|  |  | labour component/unit qty |  |  | 55.3205 |  | 27128.8931
|  |  | Add Overheads & cp and overhead charges |  | 13.61% | 7.5319 |  | 220906.7011
|  |  | labour component/unit qty (including Overheads & cp) |  |  | 62.8523 |  | 363.3334
ABSTRACT:
|  |  | A. Cost of Materials including seignorage charges |  |  |  | Rs: | 11773.0933
|  |  | B. Hire charges of Machinery |  |  |  | Rs: | 160142.973
|  |  | C. Cost of Labour |  |  |  | Rs: | 33634.835 | (Add MA if necessary))
|  |  |  | Municipal allowance | 20% |  |  | 6726.967
[7 empty] | Total Rs: | 212277.8683
|  |  | D. Add for Overheads & cp on (A+B+C) |  |  | 13.61% | Rs: | 28901.6318
|  |  | Total cost for |  | 608 | cum | Rs: | 241179.5001
|  |  | Rate per | cum | (A+B+C+D)/D2204 |  | Rs. | 396.7
| gravel top | IRR-CCDW-7-3 | Providing and filling murum / gravely soil ( CNS soil ) for foundation or above pipes
including breaking clods, spreading in layers of 10 to 15 cm, watering, compaction by power
roller to achieve density control of not less than 98 percent etc., complete with lead upto
50 m and all lifts.
|  | DATA: | For foundation filling in large area and above pipes no rehandling of soil is considered.
|  |  | Output of 1 mazdoor for spreading & levelling at site per day |  |  | : | 12 | cum
|  |  | Output of 8-10 tonne road roller for compaction per hour |  |  | : | 58.6 | cum/hour
|  |  | Cartman with double bullock cart for supplying water |  |  | : | 0.5 | day
1mazdoor for watering at site.
|  |  |  | RATE ANALYSIS |  | UNIT : | 10 | cum
A. MATERIALS:
|  |  | Sl No | Particulars | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Murum | cum | 12 | 471.6936 | 5660.3237
[6 empty] | 0 | 0 | 0
|  |  |  | Add seignorage charges on Soil @ Rs: | (Included in material rate) |  | Rs: | 0
|  |  |  | Total cost of Materials |  |  | Rs: | 5660.3237
B. MACHINERY:
|  |  | Sl No | Description | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Diesel road roller 8-10 tonne | Hour | 0.17065 | 197.2 | 33.6519
|  |  |  | Fuel / Energy charges | Hour | 0.17065 | 705.4 | 120.3754
|  |  |  | Total hire charges of Machinery |  |  | Rs: | 154.0273
C. LABOUR:
|  |  | Sl No | Description | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Operator road roller | Hour | 0.17065 | 198.4 | 33.8567
|  |  | 2 | Cartman with double bullock cart | Day | 0.5 | 440 | 220
|  |  | 3 | work inspector | Day | 0.5 | 400 | 200
|  |  | 4 | mazdoor | Day | 1.5 | 320 | 480
|  |  |  | Total cost of Labour |  |  | Rs: | 933.8567
|  |  | labour component/unit qty |  |  | 93.3857
|  |  | Add Overheads & cp and overhead charges |  | 13.61% | 12.7145
|  |  | labour component/unit qty (including Overheads & cp) |  |  | 106.1001
ABSTRACT:
|  |  | A. Cost of Materials including seignorage charges |  |  |  | Rs: | 5660.3237
|  |  | B. Hire charges of Machinery |  |  |  | Rs: | 154.0273
|  |  | C. Cost of Labour |  |  |  | Rs: | 933.8567 | (Add MA if necessary))
|  |  |  | Municipal allowance | 20% |  |  | 186.7713
[7 empty] | Total Rs: | 6934.979
|  |  | D. Add for Overheads & cp on (A+B+C) |  |  | 13.61% | Rs: | 944.1974
|  |  | Total cost for |  | 10 | cum | Rs: | 7879.1764
|  |  | Rate per | cum | (A+B+C+D)/10.0 |  | Rs. | 787.9
| Sand blanket | IRR-CAW-5-3 A | Providing and laying sand blanket below embankment including cost of all
materials, machinery, labour, spreading to specified thickness etc., complete with initial lead
upto 50 m and all lifts.
|  | DATA: | Consider 100 sqm sand blanket laying.
|  |  | Quantity of sand ( unscreened ) |  |  |  | 100 | cum
Requirement of labour for spreading collected sand.
2 mazdoors @ 10 cum / day.
|  |  |  | RATE ANALYSIS |  | UNIT : | 100 | sqm
A. MATERIALS:
|  |  | Sl No | particulars | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Sand ( unscreened ) | cum | 100 | 697.0266 | 69702.6619
[6 empty] | 0 | 0 | 0
|  |  |  | Seionorage charges for sand (included in the material rates) |  |  | Rs: | 0
|  |  |  | Total cost of Materials |  |  | Rs: | 69702.6619
B. MACHINERY:
|  |  | Sl No | Description | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Nil |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
|  |  |  | Total hire charges of Machinery |  |  | Rs: | 0
C. LABOUR:
|  |  | Sl No | Description | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | mazdoor | Day | 20 | 320 | 6400
|  |  |  | Total cost of Labour |  |  | Rs: | 6400
|  |  | labour component/unit qty |  |  | 64
|  |  | Add Overheads & cp and overhead charges |  | 13.61% | 8.7136
|  |  | labour component/unit qty (including Overheads & cp) |  |  | 72.7136
ABSTRACT:
|  |  | A. Cost of Materials including seignorage charges |  |  |  | Rs: | 69702.6619
|  |  | B. Hire charges of Machinery |  |  |  | Rs: | 0
|  |  | C. Cost of Labour |  |  |  | Rs: | 6400 | (Add MA if necessary))
|  |  |  | Municipal allowance | 20% |  |  | 1280
[7 empty] | Total Rs: | 77382.6619
|  |  | D. Add for Overheads & cp on (A+B+C) |  |  | 13.61% | Rs: | 10535.6494
|  |  | Total cost for |  | 100 | sqm | Rs: | 87918.3113
|  |  | Rate per | sqm | (A+B+C+D)/100 |  | Rs. | 879.2
| Rock toe | IRR-CAW-5-4 | Providing and constructing dry rubble rock-toe using rubble and stone chips from
approved source including cost of all materials, machinery, labour, hand packing rubble
and stone chips, finishing top and sides to required slopes etc., complete with initial lead upto
50 m and all lifts.
|  | DATA: | Top width |  |  |  | : | NIL
|  |  | Side slope upstream side |  |  |  | : | 1 (V) : 1 (H)
|  |  | Side slope down stream side |  |  |  | : | 1 (V) : 1.5 (H)
|  |  | Height |  |  |  | 1 | m
|  |  | Cross sectional area ( 0.00 + 2.50 ) x 1 / 2 |  |  |  | 1.25 | sqm
Consider 100 cum rock toe:
|  |  | Length of rock toe for 100 cum |  | ( 100 / 1.25 ) |  | : | 80 | m
Requirement of materials for 100 cum
|  |  | Rubble |  | ( 1.25 x 80 ) |  | : | 100 | cum
|  |  | Stone chips @ 15 % of rubble |  | ( 100 x 0.15 ) |  | : | 15 | cum
|  |  | Surface finishing for D / S face |  | ( 1.80 x 80 ) |  | : | 144 | sqm
Requirement of labour :
For conveying, spreading and packing :
Rock-toe material can be spread partly by dumping the material directly at spot and partly by
conveying manually. Assuming 50 % manual conveying.
|  |  | mazdoor for rubble |  |  |  | : | 10 | Nos.
|  |  | mazdoor for chips |  |  |  | : | 2 | Nos.
For packing and surface finishing.
|  |  | mazdoor |  |  |  | : | 7 | Nos.
|  |  | Mason Class-II |  |  |  | : | 7 | Nos.
|  |  |  | RATE ANALYSIS |  | UNIT : | 100 | cum
A. MATERIALS:
|  |  | Sl No | particulars | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Rubble | cum | 100 | 762.7483 | 76274.8274
|  |  | 2 | Stone chips | cum | 15 | 794.7483 | 11921.2241
|  |  | 3 | Sundries | LS | 2 | 41 | 82
|  |  |  | Seionorage charges for stone chips (included in the material rates) |  |  |  | 0
|  |  |  | Seionorage charges for stone(included in the material rates) |  |  |  | 0
|  |  |  | Total cost of Materials |  |  | Rs: | 88278.0515
B. MACHINERY:
|  |  | Sl No | Description | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Nil |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
|  |  |  | Total hire charges of Machinery |  |  | Rs: | 0
C. LABOUR:
|  |  | Sl No | Description | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | work inspector | Day | 1 | 400 | 400
|  |  | 2 | Mason Class-II | Day | 7 | 375 | 2625
|  |  | 3 | mazdoor | Day | 19 | 320 | 6080
|  |  |  | Total cost of Labour |  |  | Rs: | 9105
|  |  | labour component/unit qty |  |  | 91.05
|  |  | Add Overheads & cp and overhead charges |  | 13.61% | 12.3965
|  |  | labour component/unit qty (including Overheads & cp) |  |  | 103.4465
ABSTRACT:
|  |  | A. Cost of Materials including seignorage charges |  |  |  | Rs: | 88278.0515
|  |  | B. Hire charges of Machinery |  |  |  | Rs: | 0
|  |  | C. Cost of Labour |  |  |  | Rs: | 9105 | (Add MA if necessary))
|  |  |  | Municipal allowance | 20% |  |  | 1821
[7 empty] | Total Rs: | 99204.0515
|  |  | D. Add for Overheads & cp on (A+B+C) |  |  | 13.61% | Rs: | 13506.6316
|  |  | Total cost for |  | 100 | cum | Rs: | 112710.6831
|  |  | Rate per | cum | (A+B+C+D)/100 |  | Rs. | 1127.1
| rock fill | IRR-CAW-6-1 | Providing and constructing rockfill casing to canal embankment with graded stones and
spalls from approved quarry including cost of all materials, machinery, labour, spreading
stones and spalls in layers, hand packing, wedging, finishing surface to required slopes etc.,
complete with initial lead upto 50 m and all lifts.
|  | DATA: | Consider 100 cum rockfill casing to canal embankment.
|  |  | Quantity of rubble stones from quarry |  |  |  | : | 100 | cum
|  |  | Quantity of spalls from quarry |  |  |  | : | 15 | cum
Assume average 20 sqm surface finishing for 100 cum of rockfill.
Consider 4 Mason Cl- II and 4 mazdoors for levelling & packing rockfill.
Consider 2 Mason Cl- II and 2 mazdoors for surface finishing to slope.
Consider 2 mazdoors for supplying spalls and miscellaneous works.
|  |  |  | RATE ANALYSIS |  | UNIT : | 100 | cum
A. MATERIALS:
|  |  | Sl No | particulars | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Rubble stones ( at quarry ) | cum | 100 | 762.7483 | 76274.8274
|  |  | 2 | Stone chips / spalls ( at quarry ) |  | 15 | 794.7483 | 11921.2241
|  |  |  | Add for seignorage charges for rubble/spalls(included in the material cost) |  |  | Rs: | 0
|  |  |  | Total cost of Materials |  |  | Rs: | 88196.0515
B. MACHINERY:
|  |  | Sl No | Description | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Nil |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
|  |  |  | Total hire charges of Machinery |  |  | Rs: | 0
C. LABOUR:
|  |  | Sl No | Description | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Mason Cl- II | Day | 6 | 375 | 2250
|  |  | 2 | mazdoor | Day | 8 | 320 | 2560
|  |  |  | Total cost of Labour |  |  | Rs: | 4810
|  |  | labour component/unit qty |  |  | 48.1
|  |  | Add Overheads & cp and overhead charges |  | 13.61% | 6.5488
|  |  | labour component/unit qty (including Overheads & cp) |  |  | 54.6488
ABSTRACT:
|  |  | A. Cost of Materials including seignorage charges |  |  |  | Rs: | 88196.0515
|  |  | B. Hire charges of Machinery |  |  |  | Rs: | 0
|  |  | C. Cost of Labour |  |  |  | Rs: | 4810 | (Add MA if necessary))
|  |  |  | Municipal allowance | 20% |  |  | 962
[7 empty] | Total Rs: | 93968.0515
|  |  | D. Add for Overheads & cp on (A+B+C) |  |  | 13.61% | Rs: | 12793.7502
|  |  | Total cost for |  | 100 | cum | Rs: | 106761.8017
|  |  | Rate per | cum | (A+B+C+D)/100.0 |  | Rs. | 1067.6
| Shahabad paneling | IRR-CAW-7-26 | Providing and fixing 25 to 40 mm thick Shahabad / Talikota / other similar stone slabs
with pointing and finishing joints neatly in CM 1:3 proportion for canal / field channel lining
including cutting slabs to required size, mixing mortar, finishing joints neatly, curing etc.,
complete with lead upto 50 m and all lifts.
DATA:
|  | DATA: | Requirement of materials for 100 sqm slab lining in CM 1:3.
|  |  | Stone slabs with 5 percent allowance for breakage / wastage |  |  |  | : | 105 | sqm
|  |  | Cement mortar 1:3 propn for joints |  |  |  | : | 0.4 | cum
|  |  | Cement |  |  |  | : | 200 | kg
|  |  | Sand |  |  |  | : | 0.4 | cum
Requirement of labour for 100 sqm slab lining in CM 1:3.
|  |  | Preparing stone slabs for laying Mason Cl II |  |  |  | : | 2 | Nos.
|  |  | Laying and jointing stone slabs Mason Cl I |  |  |  | : | 4 | Nos.
|  |  | Conveying stone slabs mazdoor |  |  |  | : | 4 | Nos.
|  |  | Assisting mason for laying stones mazdoor |  |  |  | : | 2 | Nos.
|  |  | Cement mortar mixing & conveying mazdoor |  |  |  | : | 1 | No.
|  |  | Cartman with Double bullock cart for conveying water |  |  |  | : | 1 | No.
|  |  | Curing Mazdoor |  |  |  | : | 1 | No.
|  |  |  | RATE ANALYSIS |  | UNIT : | 100 | sqm
A. MATERIALS:
|  |  | Sl No | particulars | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Shahabad Stone slabs | sqm | 105 | 254.5704 | 26729.8934
|  |  | 2 | Cement 43 Gr | kg | 200 | 6.4 | 1280
|  |  | 3 | Sand ( screened ) | cum | 0.4 | 1077.7366 | 431.0946
|  |  |  | Add seignorage charges for Slabs ( included in the material cost) |  |  | Rs: | 0
|  |  |  | Add seignorage charges for sand ( included in the material cost) |  |  | Rs: | 0
|  |  |  | Total cost of Materials |  |  | Rs: | 28440.9881
B. MACHINERY:
|  |  | Sl No | Description | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | 5 hp pump ( diesel ) | Hour | 2 | 10.2 | 20.4
|  |  |  | Fuel / Energy charges | Hour | 2 | 78.4 | 156.8
|  |  |  | Total hire charges of Machinery |  |  | Rs: | 177.2
C. LABOUR:
|  |  | Sl No | Description | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Operator pump | Hour | 2 | 104.8 | 209.6
|  |  | 2 | work inspector | Day | 1 | 400 | 400
|  |  | 3 | Mason Class I | Day | 4 | 420 | 1680
|  |  | 4 | Mason Class II | Day | 2 | 375 | 750
|  |  | 5 | mazdoor | Day | 8 | 320 | 2560
|  |  | 6 | Cartman with Bullock cart for water | Day | 1 | 440 | 440
|  |  |  | Total cost of Labour |  |  | Rs: | 6039.6
|  |  | labour component/unit qty |  |  | 60.396
|  |  | Overheads & cp |  | 13.61% | 8.2229
|  |  | labour component/unit qty (including Overheads & cp) |  |  | 68.6189
ABSTRACT:
|  |  | A. Cost of Materials |  |  |  | Rs: | 28440.9881
|  |  | B. Hire charges of Machinery |  |  |  | Rs: | 177.2
|  |  | C. Cost of Labour |  |  |  | Rs: | 6039.6 | (Add MA if necessary))
|  |  |  | Municipal allowance | 20% |  |  | 1207.92
[7 empty] | Total Rs: | 35865.7081
|  |  | D. Add for Overheads & cp on (A+B+C) |  |  | 13.61% | Rs: | 4883.1162
|  |  | Total cost for |  | 100 | sqm | Rs: | 40748.8242
|  |  | Rate per | sqm | (A+B+C+D)/100.0 |  | Rs. | 407.5
| labour for cc paneling | IRR-CAW-7-27 | Fixing PCC slabs of various sizes in CM 1 : 3 proportion to the side slopes of canal
including preparing bed, flush pointing joints in CM 1 : 3 propn, cost of all materials ( excluding
PCC slabs ), labour, finishing, curing etc., complete with initial lead upto 50 m and all lifts.
DATA:
|  | DATA: | Requirement of materials for laying 100 sqm slab lining in CM 1:3. |  |  | (50mm thick)
|  |  | Cement mortar 1:3 propn for joints |  |  |  | : | 0.5 | cum
|  |  | Cement |  |  |  | : | 240 | kg
|  |  | Sand |  |  |  | : | 0.5 | cum
Requirement of labour for 100 sqm slab lining in CM 1:3.
|  |  | Laying and jointing PCC slabs Mason Cl I |  |  |  | : | 4 | Nos.
|  |  | Conveying PCC slabs mazdoor |  |  |  | : | 4 | Nos.
|  |  | Assisting mason for laying PCC slabs mazdoor |  |  |  | : | 3 | Nos.
|  |  | Cement mortar mixing & conveying mazdoor |  |  |  | : | 1 | No.
|  |  | Cartman with Double bullock cart for conveying water |  |  |  | : | 1 | No.
|  |  | Curing Mazdoor |  |  |  | : | 1 | No.
|  |  |  | RATE ANALYSIS |  | UNIT : | 100 | sqm
A. MATERIALS:
|  |  | Sl No | particulars | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Cement 43 Gr | kg | 240 | 6.4 | 1536
|  |  | 2 | Sand ( screened) | cum | 0.5 | 1077.7366 | 538.8683
|  |  |  | Add seignorage charges for sand ( included in the material cost) |  |  | Rs: | 0
|  |  |  | Total cost of Materials |  |  | Rs: | 2074.8683
B. MACHINERY:
|  |  | Sl No | Description | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | 5 hp pump ( diesel ) | Hour | 2 | 10.2 | 20.4
|  |  |  | Fuel / Energy charges | Hour | 2 | 78.4 | 156.8
|  |  |  | Total hire charges of Machinery |  |  | Rs: | 177.2
C. LABOUR:
|  |  | Sl No | Description | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Operator pump | Hour | 2 | 104.8 | 209.6
|  |  | 2 | work inspector | Day | 1 | 400 | 400
|  |  | 3 | Mason Class I | Day | 4 | 420 | 1680
|  |  | 4 | mazdoor | Day | 9 | 320 | 2880
|  |  | 5 | Cartman with Bullock cart for water | Day | 1 | 440 | 440
|  |  |  | Total cost of Labour |  |  | Rs: | 5609.6
|  |  | labour component/unit qty |  |  | 56.096
|  |  | Overheads & cp |  | 13.61% | 7.6375
|  |  | labour component/unit qty (including Overheads & cp) |  |  | 63.7335
ABSTRACT:
|  |  | A. Cost of Materials |  |  |  | Rs: | 2074.8683
|  |  | B. Hire charges of Machinery |  |  |  | Rs: | 177.2
|  |  | C. Cost of Labour |  |  |  | Rs: | 5609.6 | (Add MA if necessary))
|  |  |  | Municipal allowance | 20% |  |  | 1121.92
[7 empty] | Total Rs: | 7861.6683
|  |  | D. Add for Overheads & cp on (A+B+C) |  |  | 13.61% | Rs: | 1070.3661
|  |  | Total cost for |  | 100 | sqm | Rs: | 8932.0344
|  |  | Rate per | sqm | (A+B+C+D)/100.0 |  | Rs. | 89.3
Cement concrete(1:1.5:3) prop using 20mm gauge HG metal including cost and conveyance
of all materials and labour charges ,seign. charges etc.complete.per 10 Sq mt
|  | 0.9 | cum | 12mm HBG graded metal | Rs. | 1833.2583 | cum | 1649.9324
|  | 0.45 | cum | Sand for concrete | Rs. | 1010.7366 | cum | 454.8315
|  | 400 | Kgs | Cement | Rs. | 6400 | Kgs | 2560
|  | 0.133 | day | 1st Class Mason | Rs. | 420 | day | 55.86
|  | 0.267 | day | 2nd Class Mason | Rs. | 375 | day | 100.125
|  | 3.6 | day | Mazdoor (Both Men and Women) | Rs. | 320 | day | 1152
|  | 1 | hour | Concrete Mixer 10 / 7 cft (0.2 / 0.8 cum) capacity | Rs. | 338.6 | hour | 338.6
|  | 0.133 | Liters | Cost of Diesel for Miller | Rs. | 57 | Liters | 7.581
|  | 0.667 | Liters | Cost of Petrol for Vibrator |  | 69 | Liters | 46.023
|  | 1.2 | kl | Water (including for curing) |  | 77 | kl | 92.4
|  |  |  | Municipal allowance |  | 20% |  | 261.597
|  |  |  | Overheads & cp |  | 13.61% |  | 914.8
[5 empty] | Total rate per cum |  |  | 7633.7
| CC Planks |  | CC(1:1.5.3) panaling with 500 X500X 50mm size using 12 mm HBG
metal including cost of 14 heavy gauge welded mesh with spacing of 3" on both directions
including precasting, placing in position on inside slope of the bund and
pointing with CM(1:3) 20 mm thick including cost and conveyance of all materials and
all labour charges etc complete per 10sqmts finished item of work per 10 Sq mt
|  |  | 0.5 | Cost of CC (1:1.5:3) using 12mm |  | 7633.7 | 1cum | 3816.9 |  | Each Plank
|  |  | 5.2 | cost of welded steel mesh(14 Heavy gauge with gaps every 3") |  | 252 | kg | 1310.4 |  | 3mm
|  |  | 10 | labour for fixing of RCC slabs |  | 89.3 | Sqm | 893 | (Add MA if necessary)) | 130 gms
|  |  |  | Municipal allowance | 20% |  |  | 178.6
|  |  |  | Add 14% Overheads & CP on mesh |  | 13.61% |  | 178.411
6377.3
| grass tuffing | IRR-CAW-8-15 | Providing 10 cm Thick approved type grass turfing to the side slopes of canal including cost of
all materials ,labour,watering for minimum 15 days etc.,,complete.
with initial lead upto 50 m and all lifts ( WITHOUT USING SAND)
|  | DATA: |  | Cartmen with double bullock cart |  | : | 2 | Nos
|  |  |  | mazdoors |  | : | 8 | Nos
Unloading and laying Sods:
|  |  |  | mazdoors |  | : | 4 | Nos
Watering for 15 days:
|  |  |  | Mazdoors |  | : | 1 | Nos
|  |  |  | RATE ANALYSIS |  | UNIT : | 100 | Sqm
A. MATERIALS :
|  |  | Sl No | Particulars | Unit | Quantity | Rate in Rs | Amount in Rs
|  |  | 1 | Turfing Sods | Sqm | 100 | 28 | 2800
|  |  |  | Total Cost of materials Rs : |  |  |  | 2800
B.MACHINERY :
|  |  | Sl No | Description | Unit | Quantity | Rate in Rs | Amount in Rs
|  |  | 1 | Nill |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
|  |  |  | Total hire charges of machinery Rs : |  |  |  | 0
C.LABOUR :
|  |  | Sl No | Description | Unit | Quantity | Rate in Rs | Amount in Rs
|  |  | 1 | Mazdoor | Day | 7 | 320 | 2240
|  |  | 2 | Cart men with double bullock cart | Day | 2 | 440 | 880
|  |  |  | Total cost of labour Rs : |  |  |  | 3120
|  |  | labour component/unit qty |  |  | 31.2
|  |  | Overheads & cp |  | 13.61% | 4.368
|  |  | labour component/unit qty (including Overheads & cp) |  |  | 35.568
ABSTRACT
|  |  | A.Cost of Materials including ryolty charges |  |  |  | Rs: | 2800
|  |  | B. Hire charges of Machinery |  |  |  | Rs: | 0
|  |  | C.Cost of Labour |  |  |  | Rs: | 3120 | (Add MA if necessary))
|  |  |  | Municipal allowance | 20% |  |  | 624
[6 empty] | Total | Rs: | 6544
|  |  | D. Add for Overheads & cp on (A+B+C) |  |  | 13.61% | Rs: | 890.9656
|  |  | Total cost for |  | 100 | Sqm | Rs: | 7434.9656
|  |  | Rate per | Sqm | (A+B+C+D)/100.0 |  | Rs. | 74.3
| Gravel -Backing | IRR-CCDW-7-2 | Providing and filling murrum / gravely soil ( CNS soil ) for foundation or afloor pipes
including breaking clods, spreading in layers of 10 to 15 cm, watering, compaction by earth
masters to achieve density control of not less than 95 percent etc., complete with lead
upto 50 m and all lifts.
For foundation filling in pits and afloor pipes requires collection and rehandling of soil.
|  |  | Output of 2 mazdoors for rehandling at site per day( loose) |  |  | : | 6 | cum
|  |  | Output of 1 mazdoor for levelling & compaction / day ( loose ) |  |  | : | 12 | cum
|  |  | Cartman with double bullock cart for supplying water |  |  | : | 0.5 | day
1mazdoor for watering and miscellaneous works at site.
|  |  |  | RATE ANALYSIS |  | UNIT : | 10 | cum
A. MATERIALS:
|  |  | Sl No | Particulars | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Murum | cum | 12 | 471.6936 | 5660.3237
[6 empty] | 0 | 0 | 0
|  |  |  | Add seignorage charges on Soil @ Rs: | (Included in material rate) |  | Rs: | 0
|  |  |  | Total cost of Materials |  |  | Rs: | 5660.3237
B. MACHINERY:
|  |  | Sl No | Description | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Nill |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
|  |  |  | Total hire charges of Machinery |  |  | Rs: | 0
C. LABOUR:
|  |  | Sl No | Description | Unit | Quantity | Rate | Amount
[7 empty] | in Rs. | in Rs.
|  |  | 1 | Cartman with double bullock cart | Day | 0.5 | 440 | 220
|  |  | 2 | work inspector | Day | 0.5 | 400 | 200
|  |  | 3 | mazdoor | Day | 6 | 320 | 1920
|  |  |  | Total cost of Labour |  |  | Rs: | 2340
|  |  | labour component/unit qty |  |  | 124.35 |  |  | 234
|  |  | Overheads & cp |  | 13.61% | 16.9303
|  |  | labour component/unit qty (including Overheads & cp) |  |  | 141.2803
ABSTRACT:
|  |  | A. Cost of Materials including seignorage charges |  |  |  | Rs: | 5660.3237
|  |  | B. Hire charges of Machinery |  |  |  | Rs: | 0
|  |  | C. Cost of Labour |  |  |  | Rs: | 2340
|  |  |  | Municipal allowance | 20% |  |  | 468
[7 empty] | Total Rs: | 8468.3237
|  |  | D. Add for Overheads & cp on (A+B+C) |  |  | 13.61% | Rs: | 1153
|  |  | Total cost for |  | 10 | cum | Rs: | 9621.3237
|  |  | Rate per | cum | (A+B+C+D)/10.0 |  | Rs. | 962.1
Angulars & I Beams
Drilling of 250 mm diameter Singel Under Reamed piles for a depth of 1.80 mt with RCC(1:1.5;3) using 20 mm size HBG Metal using re1quired quantity of steel per 1 cum of concrete including cost and conveyance of all materials and all labour charges etc complete but excluding cost of steel and fabrication charges of steel per 1 No.
|  | 0.143 | cum | cost of RCC(1:1.5:3) | 7749.3 | 1cum | 1108.15
|  | 2.09 |  | Man Mazdoor | 320 | 1No | 668.8
|  |  |  | Overheads & cp @13.615% |  |  | 91.0571
[6 empty] | Total | 1868
Cost, Supply and fixing of hot dipped qalvanized iron chainlink mesh of size 50 mm X50mm(8 guage) from approved source including cost and conveyance of all materials and all labour charges etc complete
|  | 1 | Sq mt | cost of chain link mesh | 477 | 1 sq mt | 477 |  | building ssr
|  |  |  | Overheads & cp @13.615% |  |  | 64.9436
[6 empty] | Total | 541.9
Cement concrete(1:1.5:3) prop using 20mm gauge HG metal including cost and conveyance
of all materials and labour charges ,seign. charges etc.complete for fencing posts of
size 150mmX150mm at bottom and 100 mmX100 mm at top and length 2.40 mt per 1No.
|  | 0.039 |  | cost of VRCC(1:1.5:3) | 10932.9 | 1cum | 426.38
|  | 0.1 | No. | Labour charges for fixing of fencing posts | 320 | 1No. | 32
|  |  |  | Add Overheads & cp @13.615% |  |  | 4.36
[6 empty] | Total | 462.7
Drilling of 250 mm diameter Double Under Reamed piles for a depth of 3.50 mt with RCC(1:1.5;3) using 20 mm size HBG Metal using required quantity of steel per 1 cum of concrete including cost and conveyance of all materials and all labour charges etc complete but excluding cost of steel and fabrication charges of steel per 1 No.
|  | 0.28 | cum | cost of RCC(1:1.5:3) | 7749.3 | 1cum | 2169.8
|  | 4.13 |  | Man Mazdoor | 320 | 1No | 1321.6
|  |  |  | Overheads & cp @13.615% |  |  | 179.9358
[6 empty] | Total | 3671.3
Asst Engineer
RWS&S Tadepalligudem

## Hyd designs
HYDRAULIC DESIGN CALICULATIONS
CPWS Scheme to district.
1 | No.of habitations |  |  |  |  | :: | 100
2 | Population as per 2011census |  |  |  |  | :: | 100000
3 | Population in the year of commissioning (2017) |  |  |  |  | :: | 106152.0151
4 | Prospective population (2027) |  |  |  |  | :: | 117257.8645
5 | Ultimate population ( 2037) |  |  |  |  | :: | 129525.6315
6 | Per capita clear water demand |  |  |  |  | :: | 70 | LPCD
7 | Per capita raw water demand |  |  |  |  | :: | 80 | LPCD
8 | Prospective clear water demand per day |  |  |  |  | :: | 8208050.5145 | Litres
9 | Prospective Raw water demand per day |  |  |  |  | :: | 9380629.1594 | Litres
10 | Prospective clear water demand |  |  |  |  | :: | 8550.0526 | LPM | 6717.8985 | with 55 lpcd
11 | Prospective Raw water demand |  |  |  |  | :: | 9771.4887 | LPM
12 | Ultimate clear water demand per day |  |  |  |  | :: | 9066794.2048 | Litres
13 | Ultimate Raw water demand per day |  |  |  |  | :: | 10362050.5197 | Litres
14 | Ultimate clear water demand |  |  |  |  | :: | 9444.5773 | LPM
15 | Ultimate Raw water demand |  |  |  |  | :: | 10793.8026 | LPM
16 | Source |  |  |  |  | ::
17 | Intake well at Reservoir
considering 15 minutes storage capacity
| Intake well ultimate demand with 80 LPCD |  |  |  |  | :: | 10793.8026 | LPM
| Required capacity of intakewell |  |  |  |  | :: | 161907.0394 | Litres
| Required capacity of intakewell |  |  |  |  | :: | 161.907 | Cum | 235.5
1 no of intake well of 10.00 mts dia and 4.00 m depth below bed level proposed
18 | GLBR on hillock ( Raw Water)
| Population as per 2011 census | [5 empty] | 100000
| Prospective Papulation | [5 empty] | 117257.8645
| Total prospective clear water demand |  |  |  |  | :: | 9771.4887 | LPM
| Required capacity of reservoir ( 30 min.) |  |  |  |  | :: | 293144.6612 | Litres
Provide 700 KL capacitiy GLBR
17 | Rapid Sand Filters at Head works
| Prospective demand per day |  |  |  |  | :: | 8208050.5145 | lts
| Capacity of filter | [5 empty] | 12312076
[7 empty] | 12.3121 | MLD
Provide 17.00 MLD Rapid sand filters
18 | Clear Water sump at Headworks
| Clear water demand |  |  |  |  | :: | 8550.0526 | LPM
| Assume 2 1/2 hours capacity |  |  | 150 | min
| Capacity of sump required |  |  |  |  | :: | 1282507.8929 | Litres
Provide 1400 kl capacity Clear water Sump
19 | OHBR at Headworks
\ | Population as per 2011 census | [5 empty] | 100000
| Prospective Papulation | [5 empty] | 117257.8645
| Total prospective clear water demand |  |  |  |  | :: | 8550.0526 | LPM
| Required capacity of reservoir ( 30 min.) |  |  |  |  | :: | 256501.5786 | Litres
Provide 300 KL capacitiy OHBR
Pump sets
19 | From Collection well to RSF (Raw water at 80 lpcd)
| Prospective population |  |  |  |  | :: | 117257.8645
| Prospective Raw water demand |  |  |  |  | :: | 9771.4887 | LPM
| Length of pipe line | [5 empty] | 0.5 | Km
| MWL @ RSF | [5 empty] | 505
| FVL @ Collection well | [5 empty] | 485
| Friction losses | [5 empty] | 0.70753
| Add:station losses | [5 empty] | 6
| Head | [5 empty] | 26.7075 | mts. | 4885.7444
| H.P. required | [5 empty] | 96.6564 | HP
| Provide 3 nos of | 75 | HP | VT pump sets one being stand-by. |  |  |  |  | 2475000 |  | 4885.7444
20 | From HW Sump to HW OHBR
| Prospective population |  |  |  |  | :: | 117257.8645
| Prospective clear water demand |  |  |  |  | :: | 8550.0526 | LPM
| Length of pipe line | [5 empty] | 48.43 | Km
| MWL @ OHBR | [5 empty] | 550
| FVL @ Sump | [5 empty] | 480
| Friction losses | [5 empty] | 89.3346 |  | 4275.0263
| Add:station losses | [5 empty] | 6
| Head | [5 empty] | 165.3346 | mts.
| H.P. required | [5 empty] | 628.2755 | HP
| Provide 3 nos of | 400 | HP | HSC pump sets one being stand-by. |  |  |  |  | 7600000
0
0
10075000

## Design
CPWS SCHEME TO DISTRICT
1 | Total population as per 2011 census |  |  |  | 19619
| Population growth rate ( % ) |  |  |  | 1
| Estimate prepare Year |  |  |  | 2015
| Base year population |  |  | 2015 | 20416
0.80335
| Prospective population (10 years) |  |  | 2027 | 23006 |  |  |  |  | 0.90529
including 2 years for commissionig
| Ultimate population (20 years) |  |  | 2037 | 25413
including 2 years for commissionig
| Hours of Operation |  |  |  | 16
| Raw water demand |  |  |  | 80 | Lpcd
| Clear water demand |  |  |  | 70 | Lpcd | [6 empty] | 32487
[5 empty] | R.water | C.Water
| Base Year |  |  |  | 1633280 | 1429120
| Prospective demand |  |  |  | 1840480 | 1610420
| Ultimate demand |  |  |  | 2033040 | 1778910
[5 empty] | R.water | C.Water
| Base Year |  |  |  | 1701 | 1489
| Prospective demand |  | L.P.M |  | 1918 | 1678
| Ultimate demand |  | L.P.M |  | 2118 | 1854
2 |  | Summer Storage Tank
|  | Canal closer period |  | 120 | days | 243964.8 | Cum
|  | Extra Period | 0 | days for canal Uncerinity |  | 0 | Cum
[5 empty] | Total | 243964.8 | Cum
|  | Seepage & Evoparation looses @ 40% |  |  |  | 97585.92 | Cum
[5 empty] | Total | 341550.72 | Cum
[5 empty] | Net capacity | 341550.72 | Cum
3 |  | Raw water demand calculation from canal to SS tank
|  | ( for canal closer period |  | 120 | days)
|  | SS tank capacity |  |  |  | 341550.72 | Cum
|  | For regular supply of |  | 245 | days) | 498094.8 | Cum
|  |  |  | Total Qty for year |  | 839645.52 | Cum
[6 empty] | 245 | days
|  |  |  | Hours of Supply |  | 16 | 16 | 16
|  |  |  | LPM |  | 3570 | 3231.8675 | 2867.9595
|  |  | Ultimate | MLD |  | 3.4272 | 3.1026 | 2.7532
|  | Ultimate | 3570 | 3.4272 | MLD
|  | Prospective | 3231.8675 | 3.1026 | MLD
|  | Base | 2867.9595 | 2.7532 | MLD
4 |  | Raw water pipe line length |  |  |  | 600 | m
As per economical pumping main AC cl-15 350mm dia is economical
5 |  | Raw water pumping main from SST to Micro Filter
|  | Hours of Pumping |  | 16
|  | Ultime |  | 2118 | LPM | MLD | 2.033
|  | Prospective |  | 1918 | LPM | MLD | 1.8405
|  | Base |  | 1701 | LPM | MLD | 1.6333
As per economical pumping main HDPE- 4 Kg/cm2, 200mm dia is economical
100 M
6 |  | Clear water pumping main from sump to OHBR
|  | Hours of Pumping |  | 16
|  | Ultime |  | 1854 | LPM | MLD | 1.7798
|  | Prospective |  | 1678 | LPM | MLD | 1.6109
|  | Base |  | 1489 | LPM | MLD | 1.4294
As per economical pumping main AC cl-20, 250mm dia is economical
|  | are economical |  |  |  |  | 11000 M
7 |  | SS Filters
|  | Prospective daily demand |  |  | 1610.42 | Cum
|  | With 100 lts/sqmt/hr area required |  |  | 1610.42 | /(20x0.10+0.5) | 644.168 | sqmt
|  | Existing Area |  |  |  |  | 0 | sqmt
[6 empty] | Net req | 644.168 | sqmt
|  | Proposing | 26 | 13 | 3 | Area | 1014
[5 empty] | Provided area |  | 1014 | Sqmt
7 |  | Rapid Sand Filter
|  |  | Capacity Requirement |  | 1.62 | MLD
|  |  | For 24 Hours Operation |  | 2.43 | MLD
|  |  | Existing |  | 0
|  |  | Balance required |  | 2.43
|  |  | Provide | 5 | MLD
8 |  | Clear water sump | [6 empty] | Intermediate sumps for 240 min
|  | lpm | 1678
|  | Capacity required |  | 150 | minites | 251.7 | Cum
|  | Existing |  |  |  | 0
[5 empty] | Net required | 251.7 | Cum
[5 empty] | Provide | 250 | KL
9 |  | OHBR |  |  | For 70 LPCD
|  | lpm | 1678
|  | Capacity required |  | 30 | min | 50340 | Lts
Hence, Provide 60 KL OHBR with 30 mts staging
10 |  | BPT |  |  | For 55 LPCD
|  | Pros Population |  | 17613
|  | lpm | 1010
|  | Capacity required |  | 30 | min | 30300 | Lts
Hence, Provide 40 KL BPT with 15mts staging
11 |  | BPT |  |  | For 55 LPCD
|  | Pros Population |  | 34160
|  | lpm | 1958
|  | Capacity required |  | 30 | min | 58740 | Lts
Hence, Provide 60 KL BPT with 15mts staging
1 |  | OHSR's | 55 | lpcd | 1.1726 | 64.4918
|  | Sno | Hab Name | Population | OHSR-Req | Existing | Bal req | Provided
|  | 1 |  | 5455 | 175901 | 0 | 175901 | 40000
|  | 2 |  | 2072 | 66814 | 0 | 66814 | 40000
|  | 3 |  | 585 | 18864 | 0 | 18864 | 40000
|  | 4 |  | 636 | 20508 | 0 | 20508 | 40000
|  | 5 |  | 6464 | 208438 | 0 | 208438 | 40000
|  | 6 |  | 1574 | 50755 | 0 | 50755 | 40000
|  | 7 |  | 1059 | 34148 | 0 | 34148 | 40000
|  | 8 |  | 1278 | 41210 | 0 | 41210 | 40000
|  | 9 |  | 2878 | 92804 | 0 | 92804 | 40000
|  | 10 |  | 1157 | 37309 | 0 | 37309 | 40000
|  | 11 |  | 216 | 6965 | 0 | 6965 | 40000
|  | 12 |  | 439 | 14156 | 0 | 14156 | 40000
|  | 13 |  | 1590 | 51271 | 0 | 51271 | 40000
|  | 14 |  | 1010 | 32568 | 0 | 32568 | 40000
|  | 15 |  | 3456 | 111442 | 0 | 111442 | 40000
|  | 16 |  | 2234 | 72037 | 0 | 72037 | 40000
|  | 17 |  | 2695 | 86903 | 0 | 86903 | 40000
|  | 18 |  | 742 | 23926 | 0 | 23926 | 40000
|  | 19 |  | 1322 | 42629 | 0 | 42629 | 40000
|  | 20 |  | 1366 | 44048 | 0 | 44048 | 40000
|  | 21 |  | 800 | 25797 | 0 | 25797 | 40000
|  | 22 |  | 1200 | 38695 | 0 | 38695 | 40000
13 |  | Pumpsets
efficiency
| a | canal to SST |  |  | LPM | 3231.8675 | [5 empty] | if VT | 60%
[5 empty] | Head | 14 | [5 empty] | others | 50%
|  |  | H.P required |  | 3231.8675 | 14 | /4500 X0.50 | 20.1094
Head with losses
|  |  | Provide | 40 H.P | 1 No+1 Standbye |  | 2 Nos
| b | SST to Micro Filter |  |  | LPM | 1918
[5 empty] | Head | 8
|  |  | H.P required |  | 1918 | 8 | /4500 X0.50 | 6.8196
|  |  | Provide | 7.5 H.P | 1 No+1 Standbye |  | 2 Nos
| a) | Headworks sump to OHBR |  |  | LPM | 1318.4286
[5 empty] | Head | 55
|  |  | H.P required |  | 1318.4286 | 55 | /4500 X0.50 | 32.2283
|  |  | Provide | 60 H.P | 2 No+1 Standbye |  | 3 Nos
| d | Sump to OHBR
[5 empty] | LPM | 1678
[5 empty] | Head | 33 | m
|  |  | H.P required |  | 1678 | 33 | /4500 X0.50 | 24.6107
|  |  | Provide | 5 H.p | 1No+1 Standbye |  | 2 Nos
lpm

## Valve chambers
Input data
| Circular chambers |  |  |  |  | Side wall height |  | 1.3
[6 empty] | Valve Chamber dia |  | 0.9
|  | Isolated Works |  | 50% |  |  |  | 0.9 mt dia | 20196
[8 empty] | 1.05 mt dia | 23402
[8 empty] | 1.2 mt dia | 26994
[8 empty] | 1.5 mt dia | 34550
CPWS SCHEME TO DISTRICT
1.25
Top slab |  | 0.1
0.23
Side wall height |  | 1.3
Side wall thickness |  | 0.1 |  | 0.9
[7 empty] | CC(1:4:8) | 0.15
|  |  |  | 1.25 |  |  | Sand filling | 0.1
|  |  | Valve Chamber for pipe dia of |  |  | <150 mm
Concrete Mix |  |  | : M20
Steel |  |  | : Fe 415
Note : I. All dimensions are in Mts
II.Reinforcemnt detailing shall be accordance with IS-SP 34
Detailed cum abstract Estimate
Name of the Sub work: Construction of Valve Chamber | [5 empty] | 0.9 | Dia | <150 mm
[7 empty] | Est.Cost Rs | 20196
S.No | Description |  |  |  | Quantity |  | Rate | Amount
1 | Earth work excavation in all type of soils with intial lead and lift etc complete
|  | 1xp/4 | 1.25 | 1.25 | 1.55 | 1.9 | 158.8 | 302
2 | CC(1:4:8)using 40 mm HBG metal icluding Cost and conveyance of the all materials etc complete.
|  | 1xp/4 | 1.25 | 1.25 | 0.15 | 0.18 | 4503.5 | 811
3 | Filling the Foundation with sand including cost,conveyance ,watering and ramming etc complete.
|  |  | 1xp/4 | 1.25 | 0.1 | 0.12 | 937.7 | 113
4 | RCC(1:1.5:3) using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Side Wall
|  | p | 1 | 1.3 | 0.1 | 0.41 | 21438.1 | 8790
5 | RCC(1:1.5:3) using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Top Slab
| Slab | 1xp/4 |  | 1.25 | 1.25 | 1.2277
| Manhole | 1xp/4 |  | 0.23 | 0.23 | 0.041564
[5 empty] | Total | 1.1861 | 7284.3 | 864
6 | Cement plastering with CM(1:3),12mm thick including cost and conveyance of all the materials ect complete.
| Side wall inside |  | p | 0.9 | 1.3 | 3.6771
| Bottom |  | 1xp/4 | 0.9 | 0.9 | 0.63643
| Cover slab top |  | 1xp/4 | 1.25 | 1.25 | 1.2277
| Deduction |  | 1xp/4 | 0.23 | 0.23 | 0.041564
[5 empty] | Total | 5.4997 | 1491.9 | 820
7 | Supply and placing of the HYSD bars, fabrication including cost and conveyance of all the materials etc complete.
[6 empty] | 0.029074 | 60670.4 | 1764
[7 empty] | Total | 13464
| For isolated works @ 50% extra | [6 empty] | 20196
1.4
Top slab |  | 0.1
0.23
Side wall height |  | 1.3
Side wall thickness |  | 0.1 |  | 1.05
[7 empty] | CC(1:4:8) | 0.15
|  |  |  | 1.4 |  |  | Sand filling | 0.1
|  |  | Valve Chamber for pipe dia of |  |  | 150-300 mm
Concrete Mix |  |  | : M20
Steel |  |  | : Fe 415
Note : I. All dimensions are in Mts
II.Reinforcemnt detailing shall be accordance with IS-SP 34
Detailed cum abstract Estimate
Name of the Sub work: Construction of Valve Chamber | [5 empty] | 1.05 | Dia | 150-300 mm
[7 empty] | Est.Cost Rs | 23402
S.No | Description |  |  |  |  | Quantity | Rate | Amount
1 | Earth work excavation in all type of soils with intial lead and lift etc complete
|  |  | 1xp/4 | 1.4 | 1.4 | 2.387 | 158.8 | 379
2 | CC(1:4:8)using 40 mm HBG metal icluding Cost and conveyance of the all materials etc complete.
|  |  | 1xp/4 | 1.4 | 0.15 | 0.231 | 4503.5 | 1040
3 | Filling the Foundation with sand including cost,conveyance ,watering and ramming etc complete.
|  |  | 1xp/4 | 1.4 | 0.1 | 0.154 | 937.7 | 144
4 | RCC(1:1.5:3) using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Side Wall
|  |  | p | 1.15 | 1.3 | 0.46986 | 21438.1 | 10073
5 | RCC(1:1.5:3) using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Top Slab
| Slab |  | 1xp/4 | 1.4 | 1.4 | 1.54
| Manhole |  | 1xp/4 | 0.23 | 0.23 | 0.041564
[5 empty] | Total | 1.4984 | 7284.3 | 1092
6 | Cement plastering with CM(1:3),12mm thick including cost and conveyance of all the materials ect complete.
| Side wall inside |  | p | 1.05 | 1.3 | 4.29
| Bottom |  | 1xp/4 | 1.05 | 1.05 | 0.86625
| Cover slab top |  | 1xp/4 | 1.4 | 1.4 | 1.54
| Deduction |  | 1xp/4 | 0.23 | 0.23 | 0.041564
[5 empty] | Total | 6.6547 | 1491.9 | 993
7 | Supply and placing of the HYSD bars, fabrication including cost and conveyance of all the materials etc complete.
[6 empty] | 0.030985 | 60670.4 | 1880
[7 empty] | Total | 15601
| For isolated works @ 50% extra | [6 empty] | 23402
1.55
Top slab |  | 0.1
0.23
Side wall height |  | 1.3
Side wall thickness |  | 0.1 |  | 1.2
[7 empty] | CC(1:4:8) | 0.15
|  |  |  | 1.55 |  |  | Sand filling | 0.1
|  |  | Valve Chamber for pipe dia of |  |  | 300-450 mm
Concrete Mix |  |  | : M20
Steel |  |  | : Fe 415
Note : I. All dimensions are in Mts
II.Reinforcemnt detailing shall be accordance with IS-SP 34
Detailed cum abstract Estimate
Name of the Sub work: Construction of Valve Chamber | [5 empty] | 1.2 | Dia | 300-450 mm
[7 empty] | Est.Cost Rs | 26994
S.No | Description |  |  |  |  | Quantity | Rate | Amount
1 | Earth work excavation in all type of soils with intial lead and lift etc complete
|  |  | 1xp/4 | 1.55 | 1.55 | 2.9259 | 158.8 | 465
2 | CC(1:4:8)using 40 mm HBG metal icluding Cost and conveyance of the all materials etc complete.
|  |  | 1xp/4 | 1.55 | 0.15 | 0.28315 | 4503.5 | 1275
3 | Filling the Foundation with sand including cost,conveyance ,watering and ramming etc complete.
|  |  | 1xp/4 | 1.55 | 0.1 | 0.18877 | 937.7 | 177
4 | RCC(1:1.5:3) using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Side Wall
|  |  | p | 1.3 | 1.3 | 0.53114 | 21438.1 | 11387
5 | RCC(1:1.5:3) using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Top Slab
| Slab |  | 1xp/4 | 1.55 | 1.55 | 1.8877
| Manhole |  | 1xp/4 | 0.23 | 0.23 | 0.041564
[5 empty] | Total | 1.8461 | 7284.3 | 1345
6 | Cement plastering with CM(1:3),12mm thick including cost and conveyance of all the materials ect complete.
| Side wall inside |  | p | 1.2 | 1.3 | 4.9029
| Bottom |  | 1xp/4 | 1.2 | 1.2 | 1.1314
| Cover slab top |  | 1xp/4 | 1.55 | 1.55 | 1.8877
| Deduction |  | 1xp/4 | 0.23 | 0.23 | 0.041564
[5 empty] | Total | 7.8804 | 1491.9 | 1176
7 | Supply and placing of the HYSD bars, fabrication including cost and conveyance of all the materials etc complete.
[6 empty] | 0.035788 | 60670.4 | 2171
[7 empty] | Total | 17996
| For isolated works @ 50% extra | [6 empty] | 26994
1.85
Top slab |  | 0.1
0.23
Side wall height |  | 1.3
Side wall thickness |  | 0.1 |  | 1.5
[7 empty] | CC(1:4:8) | 0.15
|  |  |  | 1.85 |  |  | Sand filling | 0.1
Valve Chamber for pipe dia of
Concrete Mix |  |  | : M20
Steel |  |  | : Fe 415
Note : I. All dimensions are in Mts
II.Reinforcemnt detailing shall be accordance with IS-SP 34
Detailed cum abstract Estimate
Name of the Sub work: Construction of Valve Chamber | [5 empty] | 1.5 | Dia | 450-600 mm
[7 empty] | Est.Cost Rs | 34550
S.No | Description |  |  |  |  | Quantity | Rate | Amount
1 | Earth work excavation in all type of soils with intial lead and lift etc complete
|  |  | 1xp/4 | 1.85 | 1.85 | 4.1681 | 158.8 | 662
2 | CC(1:4:8)using 40 mm HBG metal icluding Cost and conveyance of the all materials etc complete.
|  |  | 1xp/4 | 1.85 | 0.15 | 0.40337 | 4503.5 | 1817
3 | Filling the Foundation with sand including cost,conveyance ,watering and ramming etc complete.
|  |  | 1xp/4 | 1.85 | 0.1 | 0.26891 | 937.7 | 252
4 | RCC(1:1.5:3) using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Side Wall
|  |  | p | 1.6 | 1.3 | 0.65371 | 21438.1 | 14014
5 | RCC(1:1.5:3) using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Top Slab
| Slab |  | 1xp/4 | 1.85 | 1.85 | 2.6891
| Manhole |  | 1xp/4 | 0.23 | 0.23 | 0.041564
[5 empty] | Total | 2.6475 | 7284.3 | 1929
6 | Cement plastering with CM(1:3),12mm thick including cost and conveyance of all the materials ect complete.
| Side wall inside |  | p | 1.5 | 1.3 | 6.1286
| Bottom |  | 1xp/4 | 1.5 | 1.5 | 1.7679
| Cover slab top |  | 1xp/4 | 1.85 | 1.85 | 2.6891
| Deduction |  | 1xp/4 | 0.23 | 0.23 | 0.041564
[5 empty] | Total | 10.544 | 1491.9 | 1573
7 | Supply and placing of the HYSD bars, fabrication including cost and conveyance of all the materials etc complete.
[6 empty] | 0.045923 | 60670.4 | 2786
[7 empty] | Total | 23033
| For isolated works @ 50% extra | [6 empty] | 34550

## Intakewell-canal
Input data
[6 empty] | In.well int dia |  | 3
[6 empty] | Well ht above bed level |  | 0.6
[6 empty] | Well dt.below bed level |  | 2 | Dia | Reduce
[6 empty] | Out let L.P.M |  | 3570 | 300 | 0
[6 empty] | Location |  | @ Canal
CPWS SCHEME TO DISTRICT
Top slab thickness |  | 0.1
Pump house Height |  | 3.6
Pump house side wall |  | 0.1
3.6
Bottom slab |  | 0.15
Above bed level |  | 0.6
Below bed level |  | 2 |  | 3
Wall thickness |  | 0.15
0.75
0.3
[6 empty] | VCC(1:2.5:5) | 0.2
|  |  | 5.1 |  |  | CC(1:4:8) | 0.3
[6 empty] | Sand | 0.3
|  | Raw water well cum Pump House |  |  | @ Canal
Concrete Mix |  | : M 30
Steel |  | : Fe 415
Note : I. All dimensions are in Mts
II.Reinforcement detailing shall be accordance with IS-SP 34
Detailed cum abstract estimate
CPWS SCHEME TO DISTRICT
Name of work:Construction of the Intake well cum Pump House | [6 empty] | @ Canal
[6 empty] | Est.cost Rs | 5 | Lakhs
S.No | Description |  |  |  |  | Quantity | Rate | Amount
1 | Earth work excavation in all type of soils with intial lead and lift etc complete
| 0-3 Mts | 1xp/4 | 5.1 | 5.1 | 3 | 61.31 | 158.8 | 9736
| 3-6 Mts | 1xp/4 | 5.1 | 5.1 | 0.1 | 2.04 | 204.2 | 417
| 4-6 Mts | 22/7 X 1/4 | 5.1 | 5.1 | 0 | 0 | 423.8 | 0
| 6-8 Mts | 22/7 X 1/4 | 5.1 | 5.1 | 0 | 0 | 423.8 | 0
| above 6m | 1xp/4 | 5.1 | 5.1 | 0 | 0 | 272.2 | 0
2) | Filling the Foundation with sand including cost,conveyance ,watering and ramming etc complete.
|  |  | 1xp/4 | 5.1 | 0.3 | 6.13 | 937.7 | 5748
3 | CC(1:4:8)using 40 mm HBG metal icluding Cost and conveyance of the all materials etc complete.
|  | 1xp/4 | 5.1 | 5.1 | 0.3 | 6.13 | 4470.5 | 27404
4 | VCC(1:2.5:5) using 40,20,10 mm HBG metal including cost and conveyance of all the materials etc complete for
|  | 1xp/4 | 5.1 | 5.1 | 0.2 | 4.0873 | 5442.3 | 22244
5 | M30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Well Curb
|  | p | 3.15 | 0.3 | 1.65 | 4.9005 | 10975 | 53783
6 | M30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Side Walls
| Above BL | p | 3.15 | 0.15 | 0.6 | 0.891 | 17492.5 | 15586
| below BL | p | 3.15 | 0.15 | 2 | 2.97 | 17492.5 | 51953
| below BL | p | 3.15 | 0.15 | 0 | 0 | 19295.7 | 0
7 | M30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Pump House Side Walls
|  | p | 3.15 | 0.1 | 3.6 | 3.56
| Deductions | Door | 1 | 2.1 | 1.2 | 0.25
| Deductions | Windows | 2 | 0.9 | 1.2 | 0.22
[5 empty] | Total | 3.09 | 22010.8 | 68013
8 | M30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Pump House Floor Slab-0.150 m thick
|  |  | 1xp/4 | 3.6 | 3.6 | 10.1788 | 13422 | 13662
9 | M30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Pump House Top Slab-0.10 m thick
|  |  | 1xp/4 | 3.9 | 3.9 | 11.9507 | 11620.7 | 13888
10 | Supply and placing of the HYSD bars, fabrication including cost and conveyance of all the materials etc complete.
[6 empty] | 1.093 | 60670.4 | 66313
11 | Accoproof plastering withCM(1:3) 20mm thick including cost and conveyance of all the materials ect complete.
| Bottom Slab |  | 1xp/4 | 3.6 | 3.6 | 10.1829
| Top Slab P.House |  | 1xp/4 | 3.9 | 3.9 | 11.9507
[5 empty] | Total | 22.1336 | 2436.2 | 5392
12 | Cement plastering with CM(1:3),12mm thick including cost and conveyance of all the materials ect complete.
| Side walls inside |  | p | 3.05 | 3.6 | 34.5086
| Side walls Outside |  | p | 3.25 | 3.6 | 36.7714
| Deductions | Door | 1 | 1.2 | 2.1 | 2.52
| Deductions | Windows | 2 | 0.9 | 1.2 | 2.16
[5 empty] | Total | 66.6 | 1491.9 | 9936
13 | Snowcem painting including cost and conveyance of all the materials ect complete.
| As Per above qty |  |  |  |  | 66.6 | 1202.7 | 8010
14 | Supply and placing of the MS Door& WIndows including cost and conveyance of the materials etc complete.
| Door |  |  |  | 1 No |  |  | 3500
| Windows |  |  |  | 2 Nos |  |  | 5000
15 | Supply and placing of the CI D/F Pipes and specials for inlet including cost and conveyance of the materials etc complete.
| 350 Dia pipe 2mt-1 ,0.9mt-2,0.6mt-1,Circular Bend-1,Duckfoot bend-1With 14% Contractor's Profit | [6 empty] | 108669
16 | Synthatic Enamil paint including cost and conveyance of all the materials ect complete.
| Door |  |  |  | 1 No | 4.73
| Windows |  |  |  | 2 Nos | 5.94
[6 empty] | 10.67 | 2209.7 | 2358
17 | Unforcien items | [6 empty] | 8388
[7 empty] | Total | 500000
491612

## Intakewell-SSt
Input data
[6 empty] | In.well int dia |  | 4.5
[6 empty] | Well ht above bed level |  | 3
[6 empty] | Well dt.below bed level |  | 6
[6 empty] | Out let L.P.M |  | 2118 | Dia | Reduce
[6 empty] | Location |  | @SSTank | 200 | 100
CPWS SCHEME TO DISTRICT
Top slab thickness |  | 0.1
Pump house Height |  | 3.6
Pump house side wall |  | 0.1
5.2
Bottom slab thick |  | 0.2 |  |  |  | T.B.L = | 3
0.25
Above bed level |  | 4.6
Below bed level |  | 2 |  | 4.5
Wall thickness |  | 0.2
0.75
0.45
[6 empty] | VCC(1:2.5:5) | 0.2
|  |  |  | 6.4 |  | CC(1:4:8) | 0.3
[6 empty] | Sand | 0.3
|  | Raw water well cum Pump House |  |  | SSTank
Concrete Mix |  | : M 30
Steel |  | : Fe 415
Note : I. All dimensions are in Mts
II.Reinforcement detailing shall be accordance with IS-SP 34
Detailed cum abstract estimate
| Name of work:Construction of the Collection well cum Pump House | [5 empty] | SSTank
| CPWS SCHEME TO DISTRICT |  |  |  |  | Est.cost Rs | 11.5 | Lakhs
S.No | Description |  |  |  |  | Quantity | Rate | Amount
1 | Earth work excavation in all type of soils with intial lead and lift etc complete
| 0-2 Mts | 1xp/4 | 7.6 | 7.6 | 3 | 136.15 | 158.8 | 21621
| 2-4 Mts | 1xp/4 | 7.6 | 7.6 | 0.25 | 11.35 | 204.2 | 2318
| 2-4 Mts | 1xp/4 | 7.6 | 7.6 | 0 | 0 | 272.2 | 0
2 | Filling the Foundation with sand including cost,conveyance ,watering and ramming etc complete.
|  |  | 1xp/4 | 6.4 | 0.3 | 9.65 | 937.7 | 9049
3 | CC(1:4:8)using 40 mm HBG metal icluding Cost and conveyance of the all materials etc complete.
|  | 1xp/4 | 6.4 | 6.4 | 0.3 | 9.6549 | 4470.5 | 43162
4 | VCC(1:2.5:5) using 40,20,10 mm HBG metal including cost and conveyance of all the materials etc complete for
|  | 1xp/4 | 6.4 | 6.4 | 0.2 | 6.4366 | 5442.3 | 35030
5 | M30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Well Curb
|  | p | 4.7 | 0.45 | 1.7 | 11.3001 | 10975 | 124019
6 | M30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Side Walls
| Above BL | p | 4.7 | 0.2 | 4.6 | 13.5897 | 15296.7 | 207878
| Above BL | p | 4.7 | 0.2 | 0 | 0 | 19401.4 | 0
| below BL | p | 4.7 | 0.2 | 2 | 5.9086 | 15296.7 | 90382
7 | M30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Pump House Side Walls
|  | p | 4.7 | 0.1 | 3.6 | 5.3177
| Deductions | Door | 1 | 2.1 | 1.2 | 0
| Deductions | Windows | 2 | 0.9 | 1.2 | 0
[5 empty] | Total | 5.3177 | 22010.8 | 117047
8 | M30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Pump House Top Slab-0.10 m thick
|  |  | 1xp/4 | 5.5 |  | 23.7679 | 11620.7 | 27620
9 | M30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Pump House Floor Slab-0.20 m thick
|  |  | 1xp/4 | 5.2 |  | 21.2372 | 16133.7 | 34263
10 | Supply and placing of the HYSD bars, fabrication including cost and conveyance of all the materials etc complete.
[6 empty] | 3.2055 | 60670.4 | 194481
11 | Accoproof plastering withCM(1:3) 20mm thick including cost and conveyance of all the materials ect complete.
| Bottom Slab |  | 1xp/4 | 5.2 | 5.2 | 21.2457
| Top Slab P.House |  | 1xp/4 | 5.5 | 5.5 | 23.7679
[6 empty] | 45.0136 | 2436.2 | 10966
12 | Cement plastering with CM(1:3),12mm thick including cost and conveyance of all the materials ect complete.
| Side walls inside |  | p | 4.6 | 2.7 | 39.0343
| Side walls Outside |  | p | 4.8 | 2.7 | 40.7314
| Deductions | Door | 1 | 1.2 | 2.1 | 2.52
| Deductions | Windows | 2 | 0.9 | 1.2 | 2.16
[6 empty] | 75.0857 | 1491.9 | 11202
13 | Snowcem painting including cost and conveyance of all the materials ect complete.
| As Per above qty |  |  |  |  | 75.0857 | 1202.7 | 9031
14 | Supply and placing of the MS Door& WIndows including cost and conveyance of the materials etc complete.
| Door |  |  |  | 1 No |  |  | 3500
| Windows |  |  |  | 2 Nos |  |  | 5000
15 | Supply and placing of the CI D/F Pipes and specials for inlet including cost and conveyance of the materials etc complete.
| 300 Dia pipe 2mt-1 ,0.9mt-5,0.6mt-2,Circular Bend-1,Duckfoot bend-1 | [6 empty] | 80982
16 | Synthatic Enamil paint including cost and conveyance of all the materials ect complete.
| Door |  |  |  | 1 No | 4.73
| Windows |  |  |  | 2 Nos | 5.94
[6 empty] | 10.67 | 2209.7 | 2358
17 | Electrification, balcony to intake well | [6 empty] | 100000
18 | Unforcien items | [6 empty] | 20091
[7 empty] | Total | 1150000 |  |  | 1129909

## SS Tank
|  |  | Tank capacity req = |  | 341550.72 | Cum
|  |  | Below tank capacity = |  | 171456 | Cum
|  | Mts | [5 empty] | Mts
| 3 |  |  | T.B.L |  |  | 3
|  |  |  | ---- | F.B: | 0.6
¦
| 2 | :1U.S | 0 | ¦ | 4 |  | 4.6
| 2 | :1 D.S |  | ¦D.St: | 0
| 21.4 |  |  |  | D.storage | 0 |  | 2 | Mts
Centrel cutting depth= |  | 0 | Mts
Tank dimensions = |  | 220 | 180 | Mts : | 263.5 | 223.5 | 14.6608
Storage capacity in Cent |  | 0 | Cum | E.W from centrel portion= |  | 0 | Cum
Portion
Water storage in the tank = |  | 171456 | Cum | E.W for Bund formation = |  | 49699.872 | Cum
Total storage = |  | 171456 | Cum
Dead storage = |  | 0 | Cum | Storage for prospective = |  | 140653.6381 | Cum
Live storage = |  | 171456 | Cum | Bund height = |  | 4.6 | Mts
Estimate details: |  |  |  | Dimensions:Center line |  |  |  | Prospective
Key trench earth work : |  | 7084.8 | Cum | 885.6 | Mts | 8 | Cum | 8856
Sand blanket : |  | 829.44 | Cum | 921.6 | Mts | 2.8 | Cum | 420.48
Earth work for bund : |  | 49699.872 | Cum | 885.6 | Mts | 56.12 | Cum | 49699.872
formation
Earth work for ceteral : |  | 0 | Cum | 220 | 180 | 0 | Mts
formation
Revetment for D/S : |  | 8607.2517 | Sqmt | 836.8 | Mts | 10.2859 | Mts | 8607.2517
Rock toe : |  | 287.136 | Cum | 797.6 | Mts | 0.60 X 0.60
Top bund consolidation : |  | 398.52 | Cum | 885.6 | Mts | 3
U/S rock toe : |  | 11675.034 | Sqmt | 959.6 | Mts | 12.1666 | Cum
Toe drain earth work : |  | 191.724 | Cum | 983.2 | Mts | 0.195 | Cum
Toe drain rough stone : |  | 3539.52 | Sqmt | 983.2 | Mts
Graded metal : |  | 250.668 | Cum | 928.4 | Mts | 0.90 X 0.30
E.W cosolidation extra : |  | 409.08 | Cum | 487 | Mts | 07.0 X 1.20
for rock toe U/S
CPWS SCHEME TO DISTRICT
S.no. | Description |  | Dimensions/C.line |  | Quantity | Rate | Amount
1 | SS tank Bund Stripping by machinery and disposing the excavted soil to a distance of 1000 mts , including conveyance ect, complete
1000 mts
|  | 885.6 | 21.4 | 0.2 | 3790.368 | 98.2 | 372214
2 | Earth work excavation in all type of soils up to HDR by machinery witn in radius of 5mt cut and dump Ect complete.
| Key trench |  | 885.6 | 8 | 7084.8
| Toe wall |  | 797.6 | 0.36 | 287.136
| Central bed Cutting |  |  |  | 0
[5 empty] | 7371.936 | 54 | 398085
3 | Consolidation of the Key Trench with already excavated soils by 8-10T power roller to procter density including watering with intial lead of 0.5 Km ect complete.
| Key trench portion |  | 885.6 | 8 | 7084.8 | 90.1 | 638340
4 | Consolidation of the Bund portion with already excavated soils with in the bed/Work spot and consolidation by 8-10T power roller to procter density including seignorage charges watering with intial lead of 0.5 Km ect complete. | [7 empty] | available soils |  | WHEN EXCAVATED SOILS USED
|  | 263.5 | 223.5 | 0.75 | 44169.1875 | 396.7 | 17521917
4 | Consolidation of the Bund portion with borrowed soils with a lead of 5 km and consolidation by 8-10T power roller to procter density including seignorage charges watering with intial lead of 0.5 Km ect complete. | [7 empty] | Borrowed soils
|  | 885.6 | 56.12 | 49699.872 | 49699.872 | 396.7 | 19715939
5 | Consolidation of the Top bund portion with gravel by 8-10T power roller to procter density including watering with an initial lead of 2 hectometres barricading etc.Complete (150mm thick)
|  |  | 885.6 | 3 | 398.52 | 787.9 | 313994
Gravel backing for inside Bund Side slopes including cost and conveyance of all the materials achive density not less than 95% ect complete.
|  | 836.8 | 10.2859 | 0.15 | 1291.0878 | 962.1 | 1242156
Providing CC Plank 500x500x50 mm thick with (1:1.5:3) using 12mm HBG metal for inside slopes of the bund portion on the gravel backing including wlded mesh of 14'' guage(3" both directions) cost and conveyance of the revetment, CM(1:3) pointing-20mm thick ect complete.
|  | 836.8 | 10.2859 |  | 8607.2517 | 6377.3 | 5489103
| Shear key | 2 | 836.8 | 0.5 | 836.8 | 6377.3 | 533652
Cement concrete (1:2.5:5)prop using 40 mm,0.050mm,10mm gauge HG metal including cost &conveyance etc., complete Templates/Guidewalls
| Guide walls | 30 | 9.73 | 0.3x0.23 | 24.1693 | 5442.3 | 131537 |  |  | 30
Providing CC(1:4:8) for toe wall including cost and conveyance of the revetment ect complete.
| Toe wall | 797.6 | 0.6 | 0.6 | 287.136
|  |  |  | Total | 287.136 | 4470.5 | 1283641
9 | Providing and constructing dry rubble rock-toe using rubble and stone chips from including cost and conveyance of all materials and labour charges, handpacking rubble and stone chips finishing top and sides to required slopes with an intial lead upto 50mts and all lifts (1.2*(1+4)/2)
| Rocktoe | 959.6 | 2.5 | 1.2 | 2878.8 | 1127.1 | 3244695
10 | Providing Sand Blanket including cost and conveyance of the materilas watering rolling with hand roller etc complete.
|  | 921.6 | 7.7 | 0.9 | 6386.688 | 879.2 | 5615176
11 | Providing Graded Metal including cost and conveyance of the materilas placing in position etc complete.
|  | 928.4 | 0.9 | 0.3 | 250.668 | 1067.6 | 267613
6 | Providing Grass Turfing for Out side Bund Slopes as protection work including watering for 3 months with initial lead for conveyance of water and grass etc complete.
[5 empty] | 8607.2517 | 74.3 | 639519
7 | Provision for Bailing out water |  |  |  |  | LS | 200000
8 | Outlet & Inlet Arrangement CI Pipe | [5 empty] | 20000
9 | Unforeseen items | [5 empty] | 72419
[6 empty] | Total | 57700000

## RSF
CPWS SCHEME TO DISTRICT
RAPID SAND FILTER
Construction of Rapid Gravity Filteration plant including civil, mechanical and electrical trial running etc. complete-M30 Grade concrete).
The components of the filtration plant are as per SSR 2015-16
A) | Civil Works
(All works of VRCC Shall be in M30 design mix)
1). Stilling Chamber and Areation cascade
2). Ventury flume channel with measuring device
3) Flash Mixer chamber
4) .Clariflucculator / tube settler & flocculation tanks
5). Filter house, chemical house, Alum store, laboratory office room chlorination plant room, toilet etc. (All items shall be under RCC roof only). Separate Isolated chemical house & chlorinator room has to be provided.
6). Wash water tank of suitable capacity
7) .All the doors and windows are of aluminimum make
8) .All pipes and valves in filter beds are of D.I. make & connection from Flash mixer to Tube settler / Flocculation tank, sludge disposal pipes are of D.I. make. The size of sludge disposal pipe shall be minimum of 450 mm dia with C.I pipe.
9) The bottom level of the clear water control chamber must be above G.L so as to dispose the leakage water by gravity.
10) . Clariflucculator bridge including sludge srcapping arrangement shall be with stainless steel of Grade 304 for chemical resistance and durability
11) Railing for all the components shall be provided with Stainless steel of grade 304 for a height of 0.90mts.
12).Path ways in filter beds : Middle pathway: Minimum of 1.50mts, Side pathway: Minimum of 1.20mts.
13).Flooring in filter house shall be with 12mm thick Non-skid tiles.
14).Back wash water tank shall be constrcuted at a minimum height of 1.50mts above roof slab.
15).Filtration plant building ground floor level shall be minimum of 1.20mts above height from the neary by road crust level.
16). The minimum size of entrance hall shall be 12'x13' , Lab size shall be of 10'x15', Office room size shall be of 10'x15'.
17). The water from the treatment plant shall be tested for quantity and quality simultaneously.
18). Sufficient head room shall be provided at alum tank.
19). S.S railing of grade 304 shall be provided for staircase.
20). Testing of blowers as per I.S norms.
21).All cables shall be with copper, Cable drains shall be covered with chequered plate.
22).HDPE/MDPE pipes shall be provided for water drainage .
23).Alum storage capacity shall be for minimum period of 90 days.
24). Digital water flow meters, pressure gauges shall be provided of standard make
25).Chemical house and chlorine storage system shall be constructed out side of plant
26).Pneumatic tyre wheel shall be provided for the bridge clariflocculator.
27). Min LUX levels inside the treatment plant shall be maintained.
28). The length of sludge disposal drain shall be minimum of 30mts.
29).Yard lighting shall be provided as per norms.
30).Chlorimeter vaccum type: Metito/Toshocow-Jesco/ Industrial devices.
B) | Mechanical Equipment
1)Alum dosing equipment
2)Flash mixer equipment.
3)Sludge disposal fittings by gravity
4)Filtration plant euqipment instrumentation and piping.
5)Clarifloccualation equipment (with stainless steel blades) with rotating bridge arrangeemnt etc.,
6)Wash water tank fittings and pumpsets with 100% stand by.
7)Air blower with motor 100% stand by and pipe connections.
8) Chlorination equipment and pipe connections with chlorinator of 100% standbye,Vaccum feed Gas Chlorination has to provided.
9)Spares & Tools for 2 years
10)Gaseous Chlorination with cylinders has to provided with protection measures.
C) | Electrical Equipment
1)Necessary power supply wiring to motors and switches bus bar connections as per I.E. Rules
2)Internal wiring and illumination and fittings and fixtures for internal and external lighting exhaust fans, ceiling fans etc.
3) Erecting mechanical & Electrical equipment, trial run for 90 days 23.50 hours per day testing the treated water for efficient standards and maintenance of records and imparting training to staff.
4)Supply of 6 - sets of completion plans and maintenance manual and brochures.
5)Provision towards soil investigations.
D) | Automation for flow measurements
1)Automated Lab testing equipment of internationally reputed make and consumables for one year. For filtration plants of capacity 10 MLD and more automated online testing equipment shall be installed.
2) Automation for flow of Conductivity, Turbdity,Ph value, Residual Chlorine with recording & Storage facility (Computer based) & Alaram by SMS or other methods.
3)Off - Site Supervisory and Data Accusation (OSSADA) system for Raw water and clear water measuring, recording, Off-Site Digital Display and data Transmission to Cell Phone(SMS).
Note : | 1) Alam tanks must be bound with corroision resistant material (HDPE Lining, Bitumen Coating, tiles etc)
2) Mechnical equipment for alam mixing and in floculation tank must be corrosive resistant (due to Alam)
| Capacity: | 5
| Description | Amount
| Basic Rate Rs.4.01 per litre *5000000 | 20050000 | 6180000
Increase/Decrese for cement
| (6400-6400)* 0.7/100*5*4.01*10^6/100 | 0 | 0
Increase/Decrese for Steel
| (42000-42000)* 2/100*5*4.01*10^6/1000 | 0 | 123600
| (With out Rural area allowence Due to MA) | 0 | 618000
| Sub Total | 20050000 | 6921600
| Add Overheads & CP | 2729808
| Unforeseen items | 192 | Without LS | Per MLD
| Total | 22780000 | 22779808 | 4555961.6

## Pump House
|  | Pump House of size |  | 4 | 6 | mts
5.06
|  | 7.06 |  |  |  | Top slab thickness |  | 0.15 | 0.1 | Add
[7 empty] | Top beam depth |  | 0.23
[7 empty] | Top beam breadth |  | 0.23
[7 empty] | No of coulmns |  | 6 |  | 2 | No.of columns
|  |  | 1.2 |  |  |  | Column breadth |  | 0.23 |  |  | 3x4 | 4
| 3.6 |  | 0.9 |  |  |  | Column depth |  | 0.23 |  |  | 4x6 | 6
[8 empty] | windows | 4 |  |  | 6x8 | 8
6
4
| Pump house of size |  | 4 | 6 | Mts at Village
| Concrete Mix |  |  | : M 15
| Steel |  |  | : Fe 415
Note : I. All dimensions are in Mts
II.Reinforcement detailing shall be accordance with IS-SP 34
Detailed cum abstract Estimate
Name of the work: Construction of the Pump house of size |  |  |  |  | 4 | 6 | Mts at Village
CPWS SCHEME TO DISTRICT | [5 empty] | Est.Cost Rs | 3.85 | Lakhs
Description |  |  | Dimensions |  |  | Quantity | Rate | Amount
Sl No. |  | No. | L | B | D
1 | Drilling of 250 mm diameter Double Under Reamed piles for depth of 3.50 mt with RCC (1:1.5:3) using 20 mm HBG metal using required quantity of steel per 1 cum of concrete including cost and conveyance of all materials and all labour charges etc complete including all incidental charges such as hire charges of drilling equipment and all labour charges etc comlete as per standard specification
|  | 1X1 | 0 |  |  | 0 | 3671.3 | 0
1 | Earthwork in excavation for structures as per drawing and technical specifications Clause 305.1 including setting out, construction of shoring and bracing, removal of stumps and other deleterious material and disposal upto a lead of 50 m, dressing of sides and bottom and backfilling in trenches with excavated suitable material as per Technical Specification 305 MORD / 304 MORTH
| All round |  | 20.92 | 0.6 | 0.75 | 9.414
| Ext-columns | 6 | 1.2 | 1.2 | 1.2 | 10.368
| Steps | 1 | 1.5 | 1.2 | 0.6 | 1.08
| Deduction | 6 | 0.6 | 1.2 | 0.75 | 3.24
[5 empty] | Total | 17.622 | 158.8 | 2798
2 | Filling the Foundation with sand including cost,conveyance ,watering and ramming etc complete.
| c-footings | 6 | 1.2 | 1.2 | 0.3 | 2.592
| All round | 20.92 | 0.6 | 0.15 |  | 1.8828
| Deductions | 6 | 0.6 | 1.2 | 0.15 | 0.648
[5 empty] | Total | 3.8268 | 937.7 | 3588
3 | CC(1:4:8)using 40 mm HBG metal icluding Cost and conveyance of the all materials etc complete.
| footings | 6 | 1.2 | 1.2 | 0.3 | 2.592
| All round | 20.92 | 0.6 |  | 0.15 | 1.8828
| Steps | 1 | 1.5 | 1.2 | 0.3 | 0.54
| Deductions | 6 | 1.2 | 1.2 | 0.3 | -2.592
[5 empty] | Total | 2.4228 | 4470.5 | 10831
4 | VRCC(1:1.5:3) using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Columns footing
| footings | 6 | 1.2 | 1.2 | 0.2 | 1.728
| C-Raft | 6 | 0.75 | 0.75 | 0.4 | 1.62
[5 empty] | Total | 3.348 | 8644 | 28940
5 | VRCC(1:1.5:3) using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Columns
|  | 6 | 0.23 | 0.23 | 3.37 | 1.0696 | 10571.4 | 11308
6 | VRCC(1:1.5:3) using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Beams
| Short beams | 3 | 4.23 | 0.23 | 0.23 | 0.6713
| Long beams | 2 | 6.23 | 0.23 | 0.23 | 0.65913
[5 empty] | Total | 1.3304 | 10909.7 | 14515
7 | Brick Msaonary with CM(1:6) using Second Class Bricks including cost and conveyance of all the materials etc complete
| 1st footing | 20.92 | 0.6 | 0.6 |  | 7.5312
| 2nd footings | 20.92 | 0.3 | 0.6 |  | 3.7656
| Steps 1st | 1 | 1.5 | 1.2 | 0.3 | 0.54
| Step 2nd | 1 | 1.2 | 0.9 | 0.3 | 0.324
[5 empty] | Total | 12.1608 | 5143.4 | 62548
8 | VCC(1:1.5:3) using 20 mm HBG metal including cost and conveyance of all the materials etc complete for Bed Blocks
| Over door | 1 | 0.3 | 0.23 | 0.1 | 0.0069
| Over windows | 4 | 0.3 | 0.23 | 0.1 | 0.0276
[5 empty] | Total | 0.0345 | 10932.9 | 377
9 | VRCC(1:1.5:3) using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Lintel Beams
| Over door | 1 | 1.5 | 0.23 | 0.1 | 0.0345
| Over windows | 4 | 1.35 | 0.23 | 0.1 | 0.1242
[5 empty] | Total | 0.1587 | 10932.9 | 1735
10 | VRCC(1:1.5:3) using 20 mm HBG metal for Sun Shades of Size 75 mm thick at one end 50mm other end and 600mm width ,including cost and conveyance of all the materials,but excluding the cost of the steel etc complete
| Over door | 1 | 1.5 | 0.6 | 0.0625 | 0.05625
| Over windows | 4 | 1.35 | 0.6 | 0.0625 | 0.2025
[5 empty] | Total | 0.25875 | 8625.7 | 2232
11 | VRCC(1:1.5:3) using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Roof Slab with150 mm Thick
|  |  | 1 | 5.06 | 7.06 | 35.7236 | 14870.9 | 53124
12 | Brick Msaonary with CM(1:6) using Second Class Bricks including cost and conveyance of all the materials etc complete | [8 empty] | Brick Msaonary with CM(1:6) using Second Class Bricks including cost and conveyance of all the materials etc complete
| All round | 20.92 | 0.23 | 3.37 |  | 16.22
Deductions
| Windows | 4 | 0.9 | 1.2 | 0.23 | 0.99
| Doors | 1 | 1.05 | 2 | 0.23 | 0.48
| Bed blocks | 5 | 0.23 | 0.3 | 0.23 | 0.08
| Lintels | 5 | 1.95 | 0.1 | 0.23 | 0.22
| Ventilators | 4 | 0.23 | 0.9 | 0.3 | 0.25
[5 empty] | Total | 14.2 | 5143.4 | 73036
13 | Flush Pointing with CM(1:3) including cost and conveyance of all the materials etc complete
| Allround Basement |  | 22.12 | 0.6 |  | 13.272 | 719.9 | 955
14 | Cement plastering with CM(1:5),12mm thick including cost and conveyance of all the materials ect complete.
| Out side all round |  | 21.84 | 3.6 |  | 78.62
| In side all round |  | 20 | 3.6 |  | 72
| Ceiling |  | 4 | 6 |  | 24
Deductions
| Doors | 1 | 1.05 | 2 |  | 2.1
| Windows | 4 | 0.9 | 1.2 |  | 1.08
| Ventilators | 4 | 0.3 | 0.9 |  | 0.27
[5 empty] | Total | 171.17 | 1220.1 | 20885
15 | Accoproof plastering with CM(1:5),12mm thick including cost and conveyance of all the materials ect complete.
|  | 1 | 7.06 | 5.06 |  | 35.7236 | 1619.7 | 5787
17 | Flooring with CC(1:4:8) using 40mm HBG metal for 100mm thick and Top plastering with CM(1:3) ,20mm thick including cost and conveyance of all the materials ect complete.
|  | 1 | 4 | 6 |  | 24 | 6670.4 | 16009
18 | Synthatic Enamel painting over primary coat and Enamel painting in two caots including csot and conveyance of all the materials ect complete
| Doors | 1 | 2.25 | 1.05 | 2 | 4.725
| Windows | 4 | 2.75 | 0.9 | 1.2 | 11.88
[5 empty] | Total | 16.605 | 2209.7 | 3670
19 | Painting With White Cement two coats including cost and conveyance of all the materials ect complete.
| Inside and Ceiling |  |  |  |  | 99.45 | 346.6 | 3447
20 | Snowcem painting including cost and conveyance of all the materials ect complete.
| Out Side |  |  |  |  | 75.17 | 1202.7 | 9041
21 | Supply and fixing of the Sal Wood Door of Size 1.05 X 2.00m With angular frame CR Sheet including fixtures , fasteners including csot and conveyance of the all the materials , labour charges ect complete.
[6 empty] | 1 | 4000 | 4000
22 | Supply and fixing of the Sal Wood Windows of Size 0.9 X 1.20m With angular frame CR Sheet including fixtures , fasteners including csot and conveyance of the all the materials , labour charges ect complete.
[6 empty] | 4 | 2000 | 8000
23 | Supply and fixing of the Ready made Ventilaters of Size 0.9x0.23including csot and conveyance of the all the materials , labour charges ect complete.
[6 empty] | 4 | 300 | 1200
24 | Supply and placing of the HYSD bars, fabrication including cost and conveyance of all the materials etc complete. |  |  |  |  | 0.75 | 60670.4 | 45503
25 | Unforcein items | [6 empty] | 1471
[7 empty] | Total | 385000 |  |  | 383529
Unforcen Items

## WQ
CPWS SCHEME TO DISTRICT
Detailed cum abstract Estimate
Name of the Sub work : Construction of Watch man and Operator Quarter
| CPWS SCHEME TO DISTRICT |  |  |  |  | Est.Cost Rs | 8.25 | lakhs
Sl.No | Description | Dimensions |  |  |  | Qty | Rate | Amount
|  | Nos | L | B | D
1 | Earth work excavation in all type of soils with intial lead and lift etc complete
| column footings | 12 | 1.2 | 1.2 | 1.5 | 25.92
| alround | 1 | 31.72 | 0.9 | 0.6 | 17.13
| long wall | 1 | 9.53 | 0.9 | 0.6 | 5.15
| cross walls | 4 | 2.27 | 0.9 | 0.6 | 4.9
| platform | 1 | 7 | 0.6 | 0.6 | 2.52
| deduction | 12 | 1.2 | 1.2 | 0.6 | -10.37
[5 empty] | Total | 45.25 | 158.8 | 7186
2 | Filling the Foundation with sand including cost,conveyance ,watering and ramming etc complete.
| column footings | 12 | 1.2 | 1.2 | 0.2 | 3.46
| alround | 1 | 31.72 | 0.9 | 0.2 | 5.71
| long wall | 1 | 9.53 | 0.9 | 0.2 | 1.72
| cross walls | 4 | 2.27 | 0.9 | 0.2 | 1.63
| platform | 1 | 7 | 0.6 | 0.2 | 0.84
| deduction | 12 | 1.2 | 1.2 | 0.2 | -3.46
[5 empty] | Total | 9.9 | 937.7 | 9283
3 | CC(1:4:8)using 40 mm HBG metal icluding Cost and conveyance of the all materials etc complete.
| column footings | 12 | 1.2 | 1.2 | 0.3 | 5.18
| alround | 1 | 31.72 | 0.9 | 0.3 | 8.56
| long wall | 1 | 9.53 | 0.9 | 0.3 | 2.57
| cross walls | 4 | 2.27 | 0.9 | 0.3 | 2.45
| platform | 1 | 7 | 0.6 | 0.15 | 0.63
| deduction | 12 | 1.2 | 1.2 | 0.3 | -5.18
[6 empty] | 14.21 | 4470.5 | 63526
4 | RR Masonary with CM(1:6) using rough stone (HBG) including cost and conveyance of all the materials etc complete
| first footing | 1 | 28.96 | 0.6 | 0.6 | 10.43
| second footing | 1 | 28.96 | 0.45 | 0.45 | 5.86
| third footing | 1 | 28.96 | 0.3 | 0.3 | 2.61
| long wall first footing | 1 | 8.84 | 0.6 | 0.6 | 3.18
| long wall second footing | 1 | 8.84 | 0.45 | 0.45 | 1.79
| long wall third footing | 1 | 8.84 | 0.3 | 0.3 | 0.8
| cross walls first footing | 4 | 2.04 | 0.6 | 0.6 | 2.94
| cross walls second footing | 4 | 2.04 | 0.45 | 0.45 | 1.65
| cross walls third footing | 4 | 2.04 | 0.3 | 0.3 | 0.73
| platform | 7 | 0.6 | 0.6 | 0.45 | 1.13
| platform | 7 | 0.3 | 0.45 | 0.3 | 0.28
[6 empty] | 31.4 | 3705.2 | 116343
5 | VRCC(1:1.5:3) using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Columns footing
|  | 12 | 0.4305 |  |  | 5.166 | 8644 | 44655
6 | VRCC(1:1.5:3) using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Lintel Beams
| Door 1 | 2 | 2.25 | 0.23 | 0.23 | 0.24
| Door 2 | 4 | 2.1 | 0.23 | 0.23 | 0.44
| Door 3 | 2 | 1.65 | 0.23 | 0.23 | 0.17
| Window 1 | 2 | 2.1 | 0.23 | 0.23 | 0.22
| Window 2 | 2 | 1.8 | 0.23 | 0.23 | 0.19
| ventilator | 2 | 1 | 0.23 | 0.23 | 0.11
[6 empty] | 1.37 | 10932.9 | 14978
7 | VRCC(1:1.5:3) using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Columns
| Columns | 12 | 0.23 | 0.23 | 5.03 | 3.19 | 10571.4 | 33723
8 | VRCC(1:1.5:3) using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Beams
| Beams(F) | 1 | 27.515 | 0.23 | 0.3 | 1.9
| Beams(R) | 1 | 27.515 | 0.23 | 0.3 | 1.9
[6 empty] | 3.8 | 10909.7 | 41457
9 | VRCC(1:1.5:3) using 20 mm HBG metal for Sun Shades of Size 75 mm thick at one end 50mm other end and 600mm width ,including cost and conveyance of all the materials,but excluding the cost of the steel etc complete
| Door 1 | 2 | 1.05 | 0.6 | 0.0625 | 0.08
| Window 1 | 2 | 1.2 | 0.6 | 0.0625 | 0.09
| Window 2 | 2 | 0.9 | 0.6 | 0.0625 | 0.07
[6 empty] | 0.24 | 8625.7 | 2070
10 | VRCC(1:1.5:3) using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Roof Slab with 125mm Thick
|  | 1 | 9.76 | 6.56 |  | 64.03 | 13165.9 | 84301
11 | Brick Msaonary with CM(1:6) using Second Class Bricks including cost and conveyance of all the materials etc complete
| out side | 1 | 50.78 | 0.23 | 3.15 | 36.79
| inside | 2 | 6 | 0.1 | 3.15 | 3.78
| inside | 2 | 2.5 | 0.1 | 3.15 | 1.58
Deductions
| Door 1 | 2 | 1.05 | 2 | 0.23 | -0.97
| Door 2 | 4 | 0.9 | 2 | 0.1 | -0.72
| Door 3 | 2 | 0.75 | 2 | 0.1 | -0.3
| Window 1 | 2 | 1.2 | 1.2 | 0.23 | -0.66
| Window 2 | 2 | 0.9 | 1.2 | 0.23 | -0.5
| out side Coulmns | 10 | 0.23 | 0.23 | 3 | -1.59
| Ventilators | 2 | 0.6 | 0.23 | 0.23 | -0.06
[6 empty] | 37.35 | 5143.4 | 192106
12 | Supply and fixing of the Sal Wood Door With angular frame CR Sheet including fixtures , fasteners including csot and conveyance of the all the materials , labour charges ect complete.
| Door 1 of 2.00 x 1.05 mts | 2 |  |  |  |  | 5000 | 10000
| Door 2 of 2.00 x 0.90 mts | 4 |  |  |  |  | 3500 | 14000
| Door 3 of 2.00 x 0.75 mts | 2 |  |  |  |  | 3000 | 6000
13 | Supply and fixing of the Sal Wood Windows of Size 0.9 X 1.20m With angular frame CR Sheet including fixtures , fasteners including csot and conveyance of the all the materials , labour charges ect complete.
| Window 1 of size 1.20 X 1.20 mts | 2 |  |  |  |  | 3000 | 6000
| Window 2 of size 0.90 X 1.20 mts | 2 |  |  |  |  | 2000 | 4000
14 | Flooring with CC(1:4:8) using 40mm HBG metal for 100mm thick and Top plastering with CM(1:3) ,20mm thick including cost and conveyance of all the materials ect complete.
| Hall | 2 | 2.94 | 2.94 |  | 17.29
| bed room | 2 | 3.47 | 2.94 |  | 20.4
| Kitchen | 2 | 2.44 | 1.57 |  | 7.66
| Toilets | 2 | 2.44 | 1.14 |  | 5.56
| Platform | 1 | 7 | 0.6 |  | 4.2
[6 empty] | 55.11 | 6670.4 | 36761
15 | Cement plastering with CM(1:5),12mm thick including cost and conveyance of all the materials ect complete.
| Inside & out side A/R | 1 | 114.64 |  | 3.15 | 361.12
Deductions
| Door 1 | 2 | 1.05 | 2 |  | -4.2
| Door 2 | 4 | 0.9 | 2 |  | -7.2
| Door 3 | 2 | 0.75 | 2 |  | -3
| Window 1 | 2 | 1.2 | 1.2 |  | -2.88
| Window 2 | 2 | 0.9 | 1.2 |  | -2.16
| Ventilators | 2 | 0.6 | 0.23 |  | -0.28
[6 empty] | 341.4 | 1220.1 | 41654
16 | Accoproof plastering with CM(1:5),12mm thick including cost and conveyance of all the materials ect complete.
| Roof slab | 1 | 9.76 |  | 6.56 | 64.03 | 1619.7 | 10371
17 | Painting With White Cement two coats including cost and conveyance of all the materials ect complete.
| In side alround | 1 | 82 |  | 3.15 | 258.3
Deductions
| Door 1 | 2 | 1.05 | 2 |  | -4.2
| Door 2 | 4 | 0.9 | 2 |  | -7.2
| Door 3 | 2 | 0.75 | 2 |  | -3
| Window 1 | 2 | 1.2 | 1.2 |  | -2.88
| Window 2 | 2 | 0.9 | 1.2 |  | -2.16
| Ventilators | 2 | 0.6 | 0.23 |  | -0.28
| Ceiling | 1 | 9.76 | 6.56 |  | 64.03
[6 empty] | 302.61 | 346.6 | 10488
18 | Snowcem painting including cost and conveyance of all the materials ect complete.
| Outside | 1 | 32.64 |  | 3.15 | 102.82
Deductions
| Door 1 | 2 | 1.05 | 2 |  | -4.2
| Door 2 | 4 | 0.9 | 2 |  | -7.2
| Door 3 | 2 | 0.75 | 2 |  | -3
| Window 1 | 2 | 1.2 | 1.2 |  | -2.88
| Window 2 | 2 | 0.9 | 1.2 |  | -2.16
| Ventilators | 2 | 0.6 | 0.23 |  | -0.28
[6 empty] | 83.1 | 1202.7 | 9994
19 | Synthatic Enamel painting over primary coat and Enamel painting in two caots including csot and conveyance of all the materials ect complete
| Door 1 | 2 | 1.05 | 2 |  | 4.2
| Door 2 | 4 | 0.9 | 2 |  | 7.2
| Door 3 | 2 | 0.75 | 2 |  | 3
| Window 1 | 2 | 1.2 | 1.2 |  | 2.88
| Window 2 | 2 | 0.9 | 1.2 |  | 2.16
[6 empty] | 19.44 | 2209.7 | 4296
20 | Supply and placing of the HYSD bars, fabrication including cost and conveyance of all the materials etc complete.
[6 empty] | 0.84895 | 60670.4 | 51506
21 | Supply and fixing of the Ready made Ventilaters of Size 0.9x0.23including csot and conveyance of the all the materials , labour charges ect complete. |  |  |  |  | 2 | 300 | 600
22 | Unforeseen items | [6 empty] | 9702
[8 empty] | 825000 | 815298

## GLBR flat
Input data
[9 empty] | Side wall height |  | 1.75
[9 empty] | GLSR dia |  | 4
CPWS SCHEME TO DISTRICT
4.3
Top slab |  | 0.15
Free board |  | 0.3
Side wall height |  | 1.75
Side wall thickness |  | 0.1 |  | 4
G.L
Dead storage |  | 0.15 |  |  |  | 0.3
0.6
Bottom slab thicknes |  | 0.15
[7 empty] | CC(1:4:8) | 0.3
|  |  |  | 4.8 |  |  | Sand filling | 0.3
G.L.S.R
GLBR live capacity |  |  | 16 | Cum
GLBR Total capacity |  |  | 18 | Cum
Concrete Mix |  |  | : M30
Steel |  |  | : Fe 415
Note : I. All dimensions are in Mts
II.Reinforcemnt detailing shall be accordance with IS-SP 34
Name of the Sub work: Construction of Sump of
CPWS SCHEME TO DISTRICT
[7 empty] | Est.Cost Rs | 240000
S.No | Description |  |  |  |  | Quantity | Rate | Amount
1 | Earth work excavation in all type of soils with intial lead and lift etc complete
|  | 1xp/4 | 6 | 6 | 1.35 | 38.1857 | 158.8 | 606
2 | CC(1:4:8)using 40 mm HBG metal icluding Cost and conveyance of the all materials etc complete.
|  | 1xp/4 | 6 | 6 | 0.3 | 8.4857 | 4470.5 | 37935
3 | Filling the Foundation with sand including cost,conveyance ,watering and ramming etc complete.
|  | 1xp/4 | 6 | 6 | 0.3 | 8.4857 | 937.7 | 7957
4 | M30 Grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for bottom raft
|  | 1xp/4 | 6 | 6 | 0.15 | 4.2429 | 9199.4 | 39032
5 | M30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Side walls
|  | p | 4.1 | 1.75 | 0.1 | 2.255 | 22010.8 | 49634
6 | M30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Top Slab with- 0.15 m Thckness
|  |  | 1xp/4 | 4.3 | 4.3 | 14.522 | 13422 | 19491
7 | Accoproof plastering with CM(1:3),12mm thick including cost and conveyance of all the materials ect complete.
| B-Slab |  | 1xp/4 | 4 | 4 | 12.5714
| Slab |  | 1xp/4 | 4.3 | 4.3 | 14.5279
| Inside walls |  | p | 4 | 1.75 | 22
[6 empty] | 49.0993 | 1619.7 | 7953
8 | Cement plastering with CM(1:3),12mm thick including cost and conveyance of all the materials ect complete.
|  |  | p | 4.2 | 1.75 | 23.1 | 1491.9 | 3446
9 | Snowcem painting including cost and conveyance of all the materials ect complete.
| Side wall |  | p | 4.2 | 1.75 | 23.1
| Top Slab |  | 1xp/4 | 4.3 | 4.3 | 14.522
[6 empty] | 37.622 | 1202.7 | 4525
10 | Supply and placing of the HYSD bars, fabrication including cost and conveyance of all the materials etc complete.
[6 empty] | 0.73747 | 60670.4 | 44743
11 | Man hole covers |  | 2 Nos | 2*1682 |  |  | LS | 3364
12 | CI connections | [5 empty] | LS | 15000
13 | Unforceen items | [6 empty] | 6314
[7 empty] | Total | 240000

## GLBR Dome
CPWS SCHEME TO DISTRICT
Input data
[9 empty] | Side wall height |  | 3
[9 empty] | GLSR dia |  | 6
[9 empty] | Hillock Vertical height |  | 30
Top dome thickness |  | 0.1
1
Top ring beam size |  | 0.15
0.15
Free board |  | 0.3
|  |  |  | R | 5
Side wall height |  | 3
Side wall thickness |  | 0.1 |  | 6
G.L
Dead storage |  | 0.15 |  |  |  | 0.3
0.6
Bottom slab thicknes |  | 0.3
[7 empty] | CC(1:4:8) | 0.3
|  |  |  | 6.8 |  |  | Sand filling | 0.3
|  |  |  | G.L.S.R | @ Village
GLBR live capacity |  |  | 72 | Cum
GLBR Total capacity |  |  | 76 | Cum
Concrete Mix |  |  | : M 30
Steel |  |  | : Fe 415
Note : I. All dimensions are in Mts
II.Reinforcemnt detailing shall be accordance with IS-SP 34
Name of the work:Construction of the GLSR
|  | CPWS SCHEME TO DISTRICT |  |  |  |  | Est.Cost Rs | 600000
S.No | Description |  |  |  |  | Quantity | Rate | Amount
1 | Earth work excavation in all type of soils with intial lead and lift etc complete
|  | 1xp/4 | 8 | 8 | 1.5 | 75.4286 | 158.8 | 11978
2 | CC(1:4:8)using 40 mm HBG metal icluding Cost and conveyance of the all materials etc complete.
|  | 1xp/4 | 8 | 8 | 0.3 | 15.0857 | 4470.5 | 67441
3 | Filling the Foundation with sand including cost,conveyance ,watering and ramming etc complete.
|  | 1xp/4 | 8 | 8 | 0.3 | 15.0857 | 937.7 | 14146
4 | M30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for bottom raft
|  | 1xp/4 | 8 | 8 | 0.3 | 15.0857 | 9199.4 | 138780
5 | M30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Side walls
|  | p | 6.1 | 0.1 | 3 | 5.75 | 22010.8 | 126562
6 | M30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Top Doome
|  | 2xp | 5 | 1 | 0.1 | 3.1429 | 14403.5 | 45268
7 | M30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Ring Beam
|  | p | 6.15 | 0.15 | 0.15 | 0.43489 | 10975 | 4773
8 | Accoproof plastering with CM(1:3),12mm thick including cost and conveyance of all the materials ect complete.
| B-Slab |  | 1xp/4 | 6.8 | 6.8 | 36.3314
| Dome |  | 2xp | 5 | 1 | 15.7143
| Inside walls |  | p | 6 | 3 | 56.5714
[5 empty] | Total | 108.6171 | 1619.7 | 17593
9 | Cement plastering with CM(1:3),12mm thick including cost and conveyance of all the materials ect complete.
|  |  | p | 6.2 | 3 | 58.4571 | 1491.9 | 8721
10 | Snowcem painting including cost and conveyance of all the materials ect complete.
| Side wall |  | p | 6.2 | 3 | 58.4571
| Ring Beam |  | p | 6.3 | 0.35 | 6.93
| Top Doome |  | 2xp | 5 | 1 | 31.4286
[6 empty] | 96.8157 | 1202.7 | 11644
11 | Supply and placing of the HYSD bars, fabrication including cost and conveyance of all the materials etc complete.
[6 empty] | 2.0751 | 60670.4 | 125900
12 | Man hole covers |  | 2 Nos |  |  |  | LS | 3364
13 | CI connections | [5 empty] | LS | 15000
14 | Unforceen items | [6 empty] | 8830
[7 empty] | Total | 600000

## Sump 40kl Flat
Input data
[9 empty] | Depth below G.L |  | 2.2 | 1.75 | 2 | 2.2
[9 empty] | Sump int dia |  | 5 | 3 | 4 | 5
[9 empty] | Up lift condition |  | no | 11 cum | 23 cum | 40 cum
[9 empty] | Water table Ht | Revise req | 3
| CPWS SCHEME TO DISTRICT | [7 empty] | LPM |  | 500
5.5
Top slab thickness |  | 0.15
Free Board |  | 0.25
Ht above G.L |  | 0.25 |  |  |  | Ground level
Below G.L |  | 2.2
Side wall thickness |  | 0.1 |  | 5
Dead storage |  | 0.15 |  |  |  | 0.3
Bottom slab thicknes |  | 0.2
[7 empty] | C.C(1:4:8) | 0.3
|  |  |  | 5.8 |  |  | Sand filling | 0.3
Clear water sump live capacity |  |  | 40 | Cum
Clear water sump Total capacity |  |  | 43 | Cum
Concrete Mix |  |  | : M30
Steel |  |  | : Fe 415
Note : I. All dimensions are in Mts
II.Reinforcemnt detailing shall be accordance with IS-SP 34
Detailed estimate cum abstract estimate
Name of the work: Contruction of the Sump Flat |  |  |  |  | 40000 | Lts
| CPWS SCHEME TO DISTRICT | [5 empty] | Est.Cost Rs | 350000
S.no | Description |  |  |  |  | Quantity | Rate | Amount
1 | Earth work excavation in all type of soils with intial lead and lift etc complete
| Initial | 1xp/4 | 6 | 6 | 3 | 84.86 | 158.8 | 13476
| 2 nd mattu | 1xp/4 | 6 | 6 | 0.1 | 2.83 | 204.2 | 578
| 3 rd mattu | 1xp/4 | 6 | 6 | 0 | 0 | 272.2 | 0
2 | CC(1:4:8)using 40 mm HBG metal icluding Cost and conveyance of the all materials etc complete.
|  | 1xp/4 | 5.8 | 5.8 | 0.3 | 7.93 | 4470.5 | 35451
3 | Filling the Foundation with sand including cost,conveyance ,watering and ramming etc complete.
|  | 1xp/4 | 5.8 | 5.8 | 0.3 | 7.9294 | 937.7 | 7435
4 | M30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for bottom raft
|  | 1xp/4 | 5.8 | 5.8 | 0.2 | 5.2863 | 9199.4 | 48631
5 | M30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Side walls
|  | p | 5.1 | 2.45 | 0.1 | 3.93 | 22010.8 | 86502
6 | M30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Top Slab with 0.15 thickness
|  |  | 1xp/4 | 5.5 | 5.5 | 23.77 | 13422 | 31904
7 | Accoproof plastering with CM(1:3),12mm thick including cost and conveyance of all the materials ect complete.
| Top of the slab II |  | 1xp/4 | 5.5 | 5.5 | 23.77
| Side wall inside |  | p | 5 | 2.2 | 34.57
| Bottom slab |  | 1xp/4 | 5 | 5 | 19.64
[5 empty] | Toatl | 77.98 | 1619.7 | 12630
8 | Cement plastering with CM(1:3),12mm thick including cost and conveyance of all the materials ect complete.
| Side wall Out Side |  | p | 5.2 | 0.25 | 4.09 | 1491.9 | 610
9 | Snowcem painting including cost and conveyance of all the materials ect complete.
|  |  | p | 5.2 | 0.25 | 4.0857 | 1202.7 | 491
10 | Supply and placing of the HYSD bars, fabrication including cost and conveyance of all the materials etc complete.
[6 empty] | 1.1593 | 60670.4 | 70337
11 | Man hole covers |  | 2 Nos |  |  |  |  | 3364
12 | 150 Dia pipe 2mt-1 ,0.9mt-1,0.6mt-2,Bellmouth-1,Duckfoot bend-1 | [6 empty] | 21090
13 | Unforcen items | [6 empty] | 17501
[7 empty] | Total | 350000

## Sump 60kl Flat
Input data
[9 empty] | Depth below G.L |  | 2.3 | 1.75 | 2 | 2.2
[9 empty] | Sump int dia |  | 6 | 3 | 4 | 5
[9 empty] | Up lift condition |  | no | 11 cum | 23 cum | 40 cum
[9 empty] | Water table Ht | Revise req | 3
| CPWS SCHEME TO DISTRICT | [7 empty] | LPM |  | 500
6.5
Top slab thickness |  | 0.15
Free Board |  | 0.3
Ht above G.L |  | 0.3 |  |  |  | Ground level
Below G.L |  | 2.3
Side wall thickness |  | 0.1 |  | 6
Dead storage |  | 0.15 |  |  |  | 0.3
Bottom slab thicknes |  | 0.2
[7 empty] | C.C(1:4:8) | 0.3
|  |  |  | 6.8 |  |  | Sand filling | 0.3
Clear water sump live capacity |  |  | 60 | Cum
Clear water sump Total capacity |  |  | 65 | Cum
Concrete Mix |  |  | : M30
Steel |  |  | : Fe 415
Note : I. All dimensions are in Mts
II.Reinforcemnt detailing shall be accordance with IS-SP 34
Detailed estimate cum abstract estimate
Name of the work: Contruction of the Sump Flat |  |  |  |  | 60000 | Lts
| CPWS SCHEME TO DISTRICT | [5 empty] | Est.Cost Rs | 450000
S.no | Description |  |  |  |  | Quantity | Rate | Amount
1 | Earth work excavation in all type of soils with intial lead and lift etc complete
| Initial | 1xp/4 | 6 | 6 | 3 | 84.86 | 158.8 | 13476
| 2 nd mattu | 1xp/4 | 6 | 6 | 0.1 | 2.83 | 204.2 | 578
| 3 rd mattu | 1xp/4 | 6 | 6 | 0 | 0 | 272.2 | 0
2 | CC(1:4:8)using 40 mm HBG metal icluding Cost and conveyance of the all materials etc complete.
|  | 1xp/4 | 6.8 | 6.8 | 0.3 | 10.9 | 4470.5 | 48728
3 | Filling the Foundation with sand including cost,conveyance ,watering and ramming etc complete.
|  | 1xp/4 | 6.8 | 6.8 | 0.3 | 10.8994 | 937.7 | 10220
4 | M30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for bottom raft
|  | 1xp/4 | 6.8 | 6.8 | 0.2 | 7.2663 | 9199.4 | 66845
5 | M30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Side walls
|  | p | 6.1 | 2.6 | 0.1 | 4.98 | 22010.8 | 109614
6 | M30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Top Slab with 0.15 thickness
|  |  | 1xp/4 | 6.5 | 6.5 | 33.2 | 13422 | 44561
7 | Accoproof plastering with CM(1:3),12mm thick including cost and conveyance of all the materials ect complete.
| Top of the slab II |  | 1xp/4 | 6.5 | 6.5 | 33.2
| Side wall inside |  | p | 6 | 2.3 | 43.37
| Bottom slab |  | 1xp/4 | 6 | 6 | 28.29
[5 empty] | Toatl | 104.86 | 1619.7 | 16984
8 | Cement plastering with CM(1:3),12mm thick including cost and conveyance of all the materials ect complete.
| Side wall Out Side |  | p | 6.2 | 0.3 | 5.85 | 1491.9 | 873
9 | Snowcem painting including cost and conveyance of all the materials ect complete.
|  |  | p | 6.2 | 0.3 | 5.8457 | 1202.7 | 703
10 | Supply and placing of the HYSD bars, fabrication including cost and conveyance of all the materials etc complete.
[6 empty] | 1.5566 | 60670.4 | 94441
11 | Man hole covers |  | 2 Nos |  |  |  |  | 3364
12 | 150 Dia pipe 2mt-1 ,0.9mt-1,0.6mt-2,Bellmouth-1,Duckfoot bend-1 | [6 empty] | 21090
13 | Unforcen items | [6 empty] | 18523
[7 empty] | Total | 450000

## Sump Dome
1000
CPWS SCHEME TO DISTRICT
[6 empty] | L.P.M | 1678
Top dome thickness |  | 0.1
2
Top ring beam size |  | 0.3
0.3
Free Board |  | 0.3
Ht above G.L |  | 0.3 |  |  |  | Ground level
|  |  |  | R | 8
Depth below G.L |  | 3.35
Side wall thickness |  | 0.2 |  | 10
Dead storage |  | 0.15 |  |  |  | 0.3
Bottom slab thicknes |  | 0.25
[7 empty] | c.c (1:4:8) | 0.3
|  |  |  | 11 |  |  | Sand filling | 0.3
Clear water Sump
Clear water sump live capacity |  |  | 251 | Cum
Clear water sump Total capacity |  |  | 263 | Cum
Concrete Mix |  |  | : M30
Steel |  |  | : Fe 415
Note : I. All dimensions are in Mts
II. Reinforcemnt detailing shall be accordance with IS-SP 34
CPWS SCHEME TO DISTRICT
Deatiled cum abstract Estimate | [5 empty] | Est.cost Rs | 16.75 | Lakhs
Name of the work:Construction of the Sump | [5 empty] | 251000 | Lts
S.No | Description |  |  | Quantity |  |  | Rate | Amount
1) | Earth work excavation in all type of soils with intial lead and lift etc complete
| 1 st mattu | 1xp/4 | 11.8 | 11.8 | 3 | 328.0765 | 158.8 | 52099
| 2nd mattu | 1xp/4 | 11.8 | 11.8 | 1.2 | 131.2306 | 204.2 | 26797
| 3nd mattu | 1xp/4 | 11.8 | 11.8 | 0 | 0 | 204.2 | 0
2) | CC(1:4:8)using 40 mm HBG metal icluding Cost and conveyance of the all materials etc complete.
|  | 1xp/4 | 11 | 11 | 0.3 | 28.5214 | 4470.5 | 127505
3) | Filling the Foundation with sand including cost,conveyance ,watering and ramming etc complete.
|  | 1xp/4 | 11 | 11 | 0.3 | 28.5214 | 937.7 | 26745
4) | M30 Grade Concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for bottom raft
|  | 1xp/4 | 11 | 11 | 0.25 | 23.7679 | 9199.4 | 218650
5) | M30 Grade Concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Side walls
|  | p | 10.2 | 3.65 | 0.2 | 23.4017 | 15360 | 359450
7) | M30 Grade Concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Top Doome
|  | 2 x p | 8 | 2 | 0.1 | 10.0571 | 38737.5 | 389589
8) | M30 Grade Concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Ring Beam
|  | p | 10.3 | 0.3 | 0.3 | 2.9134 | 12394.2 | 36110
9) | Accoproof plastering with CM(1:3),12mm thick including cost and conveyance of all the materials ect complete.
| Bottom Slab |  | 1xp/4 | 10 | 10 | 78.57
| Side walls inside |  | p | 10 | 3.65 | 105.29
| Top of the Doome |  | 2p | 8 | 2 | 100.57
[5 empty] | Total | 284.43 | 1619.7 | 46069
10) | Cement plastering with CM(1:3),12mm thick including cost and conveyance of all the materials ect complete.
| Side walls Out Side |  |  | 10.4 | 0.3 | 9.8057 | 1491.9 | 1463
11) | Snowcem painting including cost and conveyance of all the materials ect complete.
| Side walls Out Side |  | p | 10.4 | 0.3 | 9.8057
| Ring Beam |  | p | 10.6 | 0.7 | 23.32
| Top Doome |  | 2p | 8 | 2 | 100.5714
[5 empty] | Total | 133.6971 | 1202.7 | 16080
12) | Supply and placing of the HYSD bars, fabrication including cost and conveyance of all the materials etc complete.(Including 5% Wastage)
[6 empty] | 5.1119 | 60670.4 | 310142
13) | Supply and placing of the Manhole cover including cost and conveyance of the materials etc complete. |  |  |  | 2 Nos
3364
14) | Supply and placing of the CI D/F Pipes and specials for inlet including cost and conveyance of the materials etc complete.
| 250 Dia pipe 2mt-1 ,0.9mt-2,0.6mt-2,Bellmouth-1,Duckfoot bend-1 | [6 empty] | 56376
15) | Unforcien items | [6 empty] | 4561
[7 empty] | Total | 1675000

## Single column
Input data
|  |  |  | OHSR | yes
|  |  |  | OHSR Capacity | 10000
|  |  |  | Staging | 6
|  |  |  | Valv Ch 0.90 | 13464 |  | 40392
|  |  |  | Vlav Ch1.05 | 15601
|  |  |  | Valv Ch1.20 | 23033
|  |  |  | Valv 25% add | no
Raft require
|  |  |  | Basic rate | 65.56
|  |  |  | Cement rate | 6400
|  |  |  | Steel rate | 42000
|  |  |  | PH SSR Cem rate | 6400
|  |  |  | PH SSR steel rate | 42000
| 10000 | Lts Capacity OHSR
CPWS SCHEME TO DISTRICT
| M.W.L | 8.5 |  | Free board | 0.15
| L.W.L | 6 |  | Dead storge | 0.15
| G.L | 0
| Inlet pipe | Outlet pipe | Scour pipe | Over flow
Rec.dia | 80 | 80 | 80 | 80
Sluice valve | 1 | 1 | 1 | 0
Total
HDPE Pipe
Sluice Cost | 11025 | 11025 | 11025 | 0 | 33075
Wind Velocity | 200 | KMPH |  | Velocity | 55.56 | Pressure | 185.21
Construction of | 10000 | Lts capacity OHSR with |  | 6 | Mts staging
CPWS SCHEME TO DISTRICT
[6 empty] | Est.Cost Rs | 770000
Construction of 10000 Lts Capacity OHSR with 6 m staging with raft foundation
platering with CM(1:3) 2 coats of Whether proof emulsion painting for external surfaces ,and 3 coats of epoxy paint to inner surface of the reservoir including roof down,lettering as per Dept Direction ,S/Fof the CI D/F Pipes verticals , vlaves,Execution as per Design and drawigns supplied by the Dept , including the cost and conveyance of the all materials , Bends , Specials Ect complete including the follwing. M30 Grade Concrete
a)Balcony of 0.75mts width at floor slab level
b)C.I man hole covers with frame of size 0.60 X 0.60 mts
c)RCC mosquito proof ventilator
d)RCC phinial 1 No
e)RCC pre-cast ladder or Aluminium ladder of 0.45 mts width 2 nos
f)Water level indicator of approved pattern 1 No
g)Lightening arrestor of approved pattern 1 No complete including conductor earthing
i) The ladder shall be with M.S ladder and Verticals with HDPE of 10kg/Sqcm shall be provided as per SSR .
A) Basic cost | 10000 | X | 65.56 |  |  | : Rs | 655600
(With out Rural area allowence Due to MA) | [6 empty] | 0
B) Rate is including of raft foundation
C) Add for increse in price of cement
| 6400 | 6400 | 0.7 | 655600 |  | : Rs | 0
( 100 X 100)
D) Add for increase/ Decrease in price of Steel
| 42000 | 42000 | 2 | 655600 |  | : Rs | 0
( 1000 X 100)
E) Deduct for staging below 10 Mts by .05 Paise per Lt | [5 empty] | : Rs | -2000
F) Add or deduct for Wind Pressure
| 185.21 | 350 | 5 | 655600 |  | : Rs | -54018
( 100 X 100)
G) Cost of HDPE Pipes Vericals(63mm-10Kg/sqcm)) | [5 empty] | : Rs | 5040 | 63mm | 168
H) Cost of D.I valves |  |  |  | 3 Nos |  | : Rs | 33075
I) Cost of valve chambers |  |  |  | 3 Nos |  | : Rs | 40392
[6 empty] | Total | 678089 |  |  | 637697
J) Add Contractor's Profit |  |  |  | 13.61% |  |  | 86822
K) Provision for unforceen items | [5 empty] | : Rs | 5089
|  |  |  | Total cost |  |  | 770000 |  | 764911 |  | Dia | Valve Ch rate
[11 empty] | 0.9 | 13464 | 150
|  | Rate per lt | 76.4911 | [7 empty] | 1.05 | 15601 | 300
[11 empty] | 1.2 | 23033 | 450

## Sump rec
1159
CPWS SCHEME TO DISTRICT
[5 empty] | L.P.M | 1678
Top dome thickness | 0.075
1
Top ring beam size | 0.25
0.25
Free Board | 0.3
Ht above G.L | 0.3
5
Depth below G.L | 2.6
Side wall thickness-2nd | 0.15 |  | 6
Side wall thickness-1st Step | 0.2
Dead storage | 0.15 |  |  |  | 0.3
Bottom slab thicknes | 0.125
[8 empty] | cc( 1:4:8) | 0.3
|  |  | 6.9 |  |  |  |  | Sand filling | 0.3
Clear water Sump
Length | 25
Breadth | 25
Clear water sump live capacity |  | 1531 | Cum
Clear water sump Total capacity |  | 1625 | Cum
Concrete Mix |  | : M20
Steel |  | : Fe 415
Note : I. All dimensions are in Mts
II. Reinforcemnt detailing shall be accordance with IS-SP 34

## C well
CPWS SCHEME TO DISTRICT
8.1
Floor slab thickness |  | 0.15
0.6
Phouse side wall thickness |  | 0.15 |  |  | 4.5
8.7
Floor slab thickness |  | 0.2
|  |  | 6.35 |  | 0.9
[6 empty] | 3.34 |  |  |  | Thickness | Depth | Bed level
[8 empty] | 1st Step-From Bottom |  | 0.45 | 5 | below
[6 empty] | 5 |  | 2nd Step |  | 0.4 | 5 | above
Above Bed level |  | 18.34 | [5 empty] | 3rd Step |  | 0.35 | 5 | above
[6 empty] | 5 |  | 4th Step |  | 0.3 | 5 | above
Below bed level |  | 5 | [5 empty] | 5th Step Top |  | 0.275 | 3.34 | above
5
Ring beam |  |  |  | 6
Width | 1.65
Depth | 0.4
Collection Well
Concrete Mix |  | : M 20
Steel |  | : Fe 415
Note : I. All dimensions are in Mts | [8 empty] | Only Well | 1
II.Reinforcement detailing shall be accordance with IS-SP 34
Deatiled cum abstract estimate
Name of work:Construction of the Collection Well Cum Pump House
| CPWS SCHEME TO DISTRICT | [5 empty] | Est.cost Rs | #REF!
S.No |  | Description |  |  |  | Quantity | Rate | Amount
1 | Earth work excavation in all type of soils with intial lead and lift etc complete
|  | p | 10.95 | 10.95 | 3 | 1130.0544 | 158.8 | 179453
|  | p | 10.95 | 10.95 | 2.7 | 1017.049 | 204.2 | 207681
|  | p | 10.95 | 10.95 | 0 | 0 | 272.2 | 0
2 | CC(1:4:8)using 40 mm HBG metal icluding Cost and conveyance of the all materials etc complete.
|  | 1xp/4 | 10.95 | 10.95 | 0.3 | 28.2627 | 4470.5 | 126349
3 | M 30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Ring beam
| Rect portion | p | 7.65 | 1.65 | 0.4 | 15.8619 | 13310.5591 | 211131
4 | M 30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Side walls
| 1st step | p | 6.45 | 4 | 0.45 | 36.49 | 11665.1836 | 425663
| 1st step(Bal) | p | 6.45 | 1 | 0.45 | 9.12 | 14736.0199 | 134393
Above Bed Level
| 2nd step | p | 6.5 | 5 | 0.4 | 40.86 | 12034.669 | 491737
| 2nd step(Bal) | p | 6.5 | 0 | 0.4 | 0 | 15465.6253 | 0
| 3rd step | p | 6.55 | 3 | 0.35 | 21.62 | #REF! | #REF!
| 3rd step(Bal) | p | 6.55 | 2 | 0.35 | 14.41 | #REF! | #REF!
| 4th step | p | 6.6 | 3 | 0.3 | 18.67 | #REF! | #REF!
| 4th step(Bal) | p | 6.6 | 2 | 0.3 | 12.45 | #REF! | #REF!
| 5th step | p | 6.625 | 3 | 0.275 | 17.18 | 14459.665 | 248417
| 4th step(Bal) | p | 6.625 | 0.34 | 0.275 | 1.95 | 14612.8213 | 28495
5 | Supply and fixing of the ISMB Girders and fabriction ect complete ect
| ISMB | 450 | 4 | 5.3975 | 72.4 | 1563.116 | 56053.05 | 87617 | 1
| 2-Angel-100x100x | 6 | 4 | 1.2 | 18.4 | 476.7072 | 56053.05 | 26721 | 1
| MS Plate | 6 | p | 6.35 | 6.35 | 500.37 | 61253.05 | 30649 | 1
5 | M 30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Floor Slab with 0.2 thickness
|  |  | 1xp/4 | 8.7 | 8.7 | 59.47 | 18211.8 | 108306 | 1
6 | M 30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Pump House Side walls
|  | p | 6.75 | 3 | 0.15 | 9.55
| Door | 1 | 1.2 | 2.1 | 0.15 | -0.378
| Windows | 2 | 0.9 | 1.2 | 0.15 | -0.324
[5 empty] | Net | 8.848 | 18222.2036 | 161230
| Balance Height | p | 6.75 | 1.5 | 0.15 | 4.77 | 18375.3599 | 87650
7 | M 30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Top Slab with 0.15 thickness
|  |  | p | 8.1 | 8.1 | 51.55 | 16201.4 | 83518
8 | Cement plastering with CM(1:3),12mm thick including cost and conveyance of all the materials ect complete.
| Inside |  | p | 6.6 | 4.5 | 93.3429
| Out side |  | p | 6.9 | 4.5 | 97.5857
| Door |  | 1 | 1.2 | 2.1 | 2.52
| Windows |  | 2 | 0.9 | 1.2 | 2.16
[5 empty] | Total | 186.2486 | 1491.9 | 27786
9 | Accoproof plastering with CM(1:3),20mm thick including cost and conveyance of all the materials ect complete.
| Floor Slab |  | p | 8.7 | 8.7 | 59.4707
| Top Slab |  | p | 8.1 | 8.1 | 51.5507
[6 empty] | 111.0214 | 2436.2 | 27047
10 | Snowcem painting including cost and conveyance of all the materials ect complete.
| as per Plastering item |  |  |  |  | 186.2486 | 1202.7 | 22400
11 | Supply and fixing of the MS Door of Size 1.05 X 2.00m With angular frame including fixtures including csot and conveyance of the all the materials , labour charges ect complete.
[5 empty] | 1 No |  |  | 3500
12 | Supply and fixing of the MS Door of Size 0.90 X 1.20 m With angular frame including fixtures including csot and conveyance of the all the materials , labour charges ect complete.
[5 empty] | 2 Nos |  |  | 5000
13 | Synthatic Enamel painting over primary coat and Enamel painting in two caots including csot and conveyance of all the materials ect complete
| For door |  |  |  | 1No | 4.73
| For Windows |  |  |  | 2 Nos | 5.94
[6 empty] | 10.67 | 414.95 | 443
14 | Cement plastering with CM(1:3),12mm thick including cost and conveyance of all the materials ect complete.
| For sinking portion |  | p | 5 | 6 | 94.2857 | 1491.9 | 14066
15 | Supply and placing of the HYSD bars, fabrication including cost and conveyance of all the materials etc complete.
[6 empty] | 27.7321 | 60670.4 | 1682515
| Manhole covers | [6 empty] | 3364
| Unforeseen items | [6 empty] | #REF!
[7 empty] | Total | #REF!

## Staircase
[10 empty] | 13324 | 600
CPWS SCHEME TO DISTRICT
Name of the work: spiral stair case with Staging | [7 empty] | 30 | mts
[7 empty] | Est.Cost Rs |  | 237721
S.no | Description |  |  |  |  | Quantity | Rate | Per | Amount
1) | Earth work excavation in all type of soils
with intial lead and lift etc., complete
|  | 1x1 | 1.5 | 1.5 | 1.8 | 4.05 | 158.8 | 1 Cum | 643
2) | CC(1:4:8) using 40 mm HBG metal icluding all
materials etc., complete
|  | 1x1 | 1.5 | 1.5 | 0.3 | 0.68 | 4470.5 | 1 Cum | 3040
3) | VRCC(1:1.5:3) using 20 mm HBG metal
including cost,conveyance and labour etc
complete for Footing excluding cost of steel
|  | 1x1 | 1.5 | 1.5 | 0.2 | 0.45 | 8644 | 1 Cum | 3890
|  | =0.25/3*(1.5^2+0.6^2+((1.5+0.6)/2)^2) |  |  |  | 0.29167 | 8644 | 1 Cum | 2521
5) | M30 grade concrete using 20 mm HBG
metal including cost,conveyance
and labour etc., complete for coulmns
excluding cost of steel
| Below G.L | 1x1 | 0.5 | 0.5 | 0.75 | 0.19
| 0 - 3 Mts | 1xπ/4 | 0.4 | 0.4 | 3 | 0.38
[6 empty] | 0.57 | 27412.4877 | 1 Cum | 15625
| 3 - 4 Mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 27564.7318 | 1 Cum | 3583 |  | #REF!
| 4 - 5 Mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 27716.9759 | 1 Cum | 3603
| 5 - 6 Mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 27869.22 | 1 Cum | 3623
| 6-7 Mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 28021.4641 | 1 Cum | 3643
| 7-8 Mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 28173.7082 | 1 Cum | 3663
| 8-9 Mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 28325.9523 | 1 Cum | 3682
| 9-10 Mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 28478.1964 | 1 Cum | 3702
| 10-11 Mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 28630.4405 | 1 Cum
| 11-12 Mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 28782.6846 | 1 Cum
| 12-13mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 28934.9287 | 1 Cum
| 13-14mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 29087.1728 | 1 Cum
| 14-15mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 29239.4169 | 1 Cum
| 15-16mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 29391.661 | 1 Cum
| 16-17mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 29543.9051 | 1 Cum
| 17-18mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 29696.1492 | 1 Cum
| 18-19mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 29848.3933 | 1 Cum
| 19-20mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 30000.6374 | 1 Cum
| 20-21mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 30152.8815 | 1 Cum
| 21-22mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 30305.1256 | 1 Cum
| 22-23mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 30457.3697 | 1 Cum
| 23-24mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 30609.6138 | 1 Cum
| 24-25mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 30761.8579 | 1 Cum
| 25-26mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 30914.102 | 1 Cum
| 26-27mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 31066.3461 | 1 Cum
| 27-28mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 31218.5902 | 1 Cum
| 28-29mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 31370.8343 | 1 Cum
| 29-30mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 31523.0784 | 1 Cum
| 30 -31mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 31675.3225 | 1 Cum
| 31 - 32mts | 1xπ/4 | 0.4 | 0.4 | 1 | 0.13 | 31827.5666 | 1 Cum
| 32 -33mts | 1xπ/4 | 0.4 | 0.4 | 0.4 | 0.05 | 31979.8107 | 1 Cum
6) | M 30 grade concrete using 20 mm HBG metal including cost,conveyance
and labour etc., complete for tie braces
excluding cost of steel 0 - 5 Mts
|  | 2 | 1.6 | 0.3 | 0.3 | 0.29 | 25588.7 | 1 Cum | 7421
| 5- 8 Mts | 1 | 1.6 | 0.3 | 0.3 | 0.14 | 26045.4323 | 1 Cum | 3646
| 8- 11 Mts | 1 | 1.6 | 0.3 | 0.3 | 0.14 | 26502.1646 | 1 Cum | 3710
| 11- 14 Mts | 1 | 1.6 | 0.3 | 0.3 | 0.14 | 26958.8969 | 1 Cum | 3774
| 14- 17 mts | 1 | 1.6 | 0.3 | 0.3 | 0.14 | 27415.6292 | 1 Cum
| 17- 20 Mts | 1 | 1.6 | 0.3 | 0.3 | 0.14 | 27872.3615 | 1 Cum
| 20-23 Mts | 1 | 1.6 | 0.3 | 0.3 | 0.14 | 28329.0938 | 1 Cum
| 23-26 | 1 | 1.6 | 0.3 | 0.3 | 0.14 | 28785.8261 | 1 Cum
| 26-29 | 1 | 1.6 | 0.3 | 0.3 | 0.14 | 29242.5584 | 1 Cum
| 29-32 | 1 | 1.6 | 0.3 | 0.3 | 0.14 | 29699.2907 | 1 Cum
7) | M30 grade concrete using 20 mm HBG
metal including cost,conveyance
and labour etc., complete for Treads
excluding cost of steel 0 - 5 Mts
|  | 34 | 0.8 | 0.2505 | 0.05 | 0.34 | 21773.6096 | 1 Cum | 7403
| 5- 8 Mts | 20 | 0.8 | 0.2505 | 0.05 | 0.2 | 22230.3419 | 1 Cum | 4446
| 8- 11 Mts | 20 | 0.8 | 0.2505 | 0.05 | 0.2 | 22687.0742 | 1 Cum | 4537
| 11- 14 Mts | 20 | 0.8 | 0.2505 | 0.05 | 0.2 | 23143.8065 | 1 Cum | 4629
| 14- 17 mts | 20 | 0.8 | 0.2505 | 0.05 | 0.2 | 23600.5388 | 1 Cum
| 17- 20 Mts | 20 | 0.8 | 0.2505 | 0.05 | 0.2 | 24057.2711 | 1 Cum
| 20-23 Mts | 20 | 0.8 | 0.2505 | 0.05 | 0.2 | 24514.0034 | 1 Cum
| 23- 26 Mts | 20 | 0.8 | 0.2505 | 0.05 | 0.2 | 24970.7357 | 1 Cum
| 26-29 Mts | 20 | 0.8 | 0.2505 | 0.05 | 0.2 | 25427.468 | 1 Cum
| 29- 32 Mts | 20 | 0.8 | 0.2505 | 0.05 | 0.2 | 25884.2003 | 1 Cum
| 32-32.40 mts | 7 | 0.8 | 0.2505 | 0.05 | 0.07 | 26340.9326 | 1 Cum
8) | M 30 grade concrete using 20 mm HBG
metal including cost,conveyance
and labour etc., complete for Risers
excluding cost of steel 0 - 5 Mts
|  | 34 | 0.8 | 0.05 | 0.15 | 0.2 | 21773.6096 | 1 Cum | 4355
| 5- 8 Mts | 20 | 0.8 | 0.05 | 0.15 | 0.12 | 25194.8188 | 1 Cum | 3023
| 8- 11 Mts | 20 | 0.8 | 0.05 | 0.15 | 0.12 | 25651.5511 | 1 Cum | 3078
| 11- 14 Mts | 20 | 0.8 | 0.05 | 0.15 | 0.12 | 26108.2834 | 1 Cum | 3133
| 14- 17 mts | 20 | 0.8 | 0.05 | 0.15 | 0.12 | 26565.0157 | 1 Cum
| 17- 20 Mts | 20 | 0.8 | 0.05 | 0.15 | 0.12 | 27021.748 | 1 Cum
| 20-23 Mts | 20 | 0.8 | 0.05 | 0.15 | 0.12 | 27478.4803 | 1 Cum
| 23- 26 Mts | 20 | 0.8 | 0.05 | 0.15 | 0.12 | 27935.2126 | 1 Cum
| 26-29 Mts | 20 | 0.8 | 0.05 | 0.15 | 0.12 | 28391.9449 | 1 Cum
| 29-32 Mts | 20 | 0.8 | 0.05 | 0.15 | 0.12 | 28848.6772 | 1 Cum
| 32-32.4 Mts | 7 | 0.8 | 0.05 | 0.15 | 0.04 | 29305.4095 | 1 Cum
9) | M 30 grade concrete using 20 mm HBG metal
including cost,conveyance and labour etc.complete
| for top slab | 100 | excluding cost steel
| steel | 1x1 | 1 | 1 | 0.1 | 0.1 | 108969.5 | 1 Cum | 10897
10) | Add cost of reiforcing steel |  |  |  |  | 0.92494 | 60670.4 | MT | 56117
11) | Cement plastering with CM(1:3) 12 mm thick
etc., complete
| For treads of steps | 2x221 | 0.8 | 0.25 |  | 88.4
| For risers of steps | 2x221 | 0.8 |  | 0.15 | 53.04
| At landing on top | 1x2 | 1 | 1 |  | 2
| Tie Braces | 1x11 | 1.8 | 1.2 |  | 23.76
| For column | 1xπ | 0.4 | 27.85 |  | 34.9973
[5 empty] | Toatl | 202.1973 | 1491.9 | 10 Sqm | 30166
12) | Snowcem paint including all materials etc., complete
| as per above iteam |  |  |  |  | 202.1973 | 1202.7 | 10 Sqm | 24318
13) | Hand railing on top slab and sides of bottom slab |  |  |  |  | 79 | 150 | 1 RMT | 11850
Unforcen item
[7 empty] | Total |  | 237721

## Shaft type
Input data
Staging | 30
Inlet lpm | 3500
Outlet LPM | 3500 | [9 empty] | Total Coulmn Ht |  | 29.85
Val Ch 0.90 | 13464
Valv Ch1.05 | 15601
Valv Ch1.20 | 17996
Valv Ch1.50 | 23033 |  |  |  |  | 1.9
Capacity | 120 | KL
[10 empty] | Total Area | 23.7679
[10 empty] | Central Opeing | 9.35
14.4179
[10 empty] | 1/3 Area | 7.21
5.5
| Stagging |  |  | 30 | mt
| Raft Dia ( foundatio) |  |  | 7.6 | mt
| Depth of foundation inclu raft |  |  | 2.5 | mt
| Raft slab depth |  |  | 0.6 | mt
| Shaft dia |  |  | 5.5 | C/c
| Sahft thickness above GL |  |  | 0.2
| Sahft thickness below GL |  |  | 0.3
| Bottom dome Radius of curvature |  |  | 5.18 | mt
| raise of the bottom dome |  |  | 0.79 | mt
| Thickness of the bottom dome |  |  | 0.3 | mt
Tank Bottom ring beam
| Width |  |  | 0.3
| Depth |  |  | 0.4
| Conical side wall Avg dia |  |  | 8.1
| Conical side wall thickness |  |  | 0.2
| Conical side wall length |  |  | 3.68
| Conical side wall height |  |  | 2.6
Top Ring beam
| Width |  |  | 0.3
| Depth |  |  | 0.4
| Dia |  |  | 10.7
Top Doome
| Radius of curvature |  |  | 9.85
| Raise of the dome |  |  | 1.5
| thickness of the dome |  |  | 0.125
Inner Shaft
| Dia |  |  | 1.2
| Shaft Length |  |  | 1.55
| Thickness |  |  | 0.15
| Flat portion | Width |  | 0.6
|  | Tank Capacity |  | 120000 | OHBR | Staging | 30
30
|  | M.W.L | 32.3 |  | Free board | 0.15 |  | 2.6
|  | L.W.L | 30 |  | Dead storge | 0.15
|  | G.L | 0
|  | Inlet pipe | Outlet pipe | Scour pipe | Over flow
| Rec.dia | 350 | 350 | 80 | 350
| 2 Mt pipe | 16 | 15 | 14 | 16
| 0.90 Mt pipe | 0 | 0 | 1 | 0
| 0.60 Mt pip | 1.3 | 1 | 1.85 | 1.3
| Duck foot bend | 1 | 1 | 1 | 1
| Bell mouth | 1 | 1 | 1 | 1
| Sluice valve | 1 | 1 | 1 | 0
|  | 58 | 926.59 | 53742.22
|  | 20 | 139.21 | 2784.2
64440
Total
| CI Sp.Cost | 391017.561 | 365927.87 | 55045.6456 | 391017.561 | 1203009
| Slucivalve Cost | 94238 | 94238 | 11025 | 0 | 199501
[12 empty] | 8965 | 600
CPWS SCHEME TO DISTRICT
Detailed estimate cum abstract estimate
Name of the work:Contruction of |  |  | 120000 | Lts capacity | OHBR | staging | 30 | Mts | Rs | 9775000
[7 empty] | Est.Cost Rs |  |  | 9775000
S.no | Description |  |  |  |  | Quantity | Rate | Per |  | Amount
1 | Earth work excavation in all type of soils
with intial lead and lift etc., complete
| Initial | 0.7854 | 7.6 | 7.6 | 3 | 136.0938 | 158.8 | 1 | Cum | 21612
|  | 0.7854 | 7.6 | 7.6 | 0.1 | 4.5365 | 204.2 | 1 | Cum | 926
2 | Sand filling the basement including watering
ramming etc., complete
| foundation | 0.7854 | 7.6 | 7.6 | 0.3 | 13.6094
[6 empty] | 13.6094 | 937.7 | 1 | Cum | 12762
3 | CC(1:4:8) using 40 mm HBG metal icluding all
materials etc., complete
|  | 0.7854 | 6.9 | 6.9 | 0.3 | 11.2178 | 4470.5 | 1 | Cum | 50149
4 | M 30 grade concrete using 20 mm HBG metal
including cost,conveyance and labour etc
complete for raft excluding cost of steel
|  | 0.7854 | 7.6 | 7.6 | 0.6 | 27.2188 | 9199.4 | 1 | Cum | 250396
5 | M 30 grade concrete using 20 mm HBG metal
including cost,conveyance and labour etc
complete for shaft
| Below GL | 3.1416 | 5.8 | 0.3 | 1.9 | 10.3861 | 21441.7 | 1 | Cum | 222696
6 | M 30 grade concrete using 20 mm HBG metal
including cost,conveyance and labour etc
complete for ring beam over door
|  | 1 | 7.8 | 0.3 | 0.3 | 0.702 | 25588.7 | 1 | Cum | 17963
7 | M 30 grade concrete using 20 mm HBG metal
metal including cost,conveyance
and labour etc., complete for shaft
excluding cost of steel
| 0 - 3 Mts | 3.1416 | 5.7 | 0.2 | 3 | 10.7442
| deduct door | 1x1 | 1.2 | 0.2 | 2.1 | 0.504
[6 empty] | 10.2402 | 27808 | 1 | Cum | 284761
| 3 - 4 Mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 27960.2 | 1 | Cum | 100137
| 4 - 5 Mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 28112.4 | 1 | Cum | 100682
| 5 - 6 Mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 28264.6 | 1 | Cum | 101227
| 6-7 Mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 28416.8 | 1 | Cum | 101772
| 7-8 Mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 28569 | 1 | Cum | 102317
| 8-9 Mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 28721.2 | 1 | Cum | 102863
| 9-10 Mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 28873.4 | 1 | Cum | 103408
| 10-11 Mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 29025.6 | 1 | Cum | 103953
| 11-12 Mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 29177.8 | 1 | Cum | 104498
| 12-13mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 29330 | 1 | Cum | 105043
| 13-14mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 29482.2 | 1 | Cum | 105588
| 14-15mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 29634.4 | 1 | Cum | 106133
| 15-16mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 29786.6 | 1 | Cum | 106678
| 16-17mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 29938.8 | 1 | Cum | 107223
| 17-18mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 30091 | 1 | Cum | 107768
| 18-19mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 30243.2 | 1 | Cum | 108313
| 19-20mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 30395.4 | 1 | Cum | 108859
| 20-21mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 30547.6 | 1 | Cum | 109404
| 21-22mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 30699.8 | 1 | Cum | 109949
| 22-23mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 30852 | 1 | Cum | 110494
| 23-24mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 31004.2 | 1 | Cum | 111039
| 24-25mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 31156.4 | 1 | Cum | 111584
| 25-26mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 31308.6 | 1 | Cum | 112129
| 26-27mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 31460.8 | 1 | Cum | 112674
| 27-28mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 31613 | 1 | Cum | 113219
| 28-29mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 31765.2 | 1 | Cum | 113764
| 29-30mts | 3.1416 | 5.7 | 0.2 | 1 | 3.5814 | 31917.4 | 1 | Cum | 114309
8 | M 30 grade concrete using 20 mm HBG metal
including cost,conveyance and labour etc.complete
| for bottom | Dome | excluding cost steel
|  | 6.2832 | 5.18 | 0.79 | 0.3 | 7.7136 | 24798.6 | 1 | Cum | 191287
9 | M 30 grade concrete using 20 mm HBG metal
including cost,conveyance and labour etc.complete
| for bottom | Ring beam | excluding cost steel
|  | 3.1416 | 5.8 | 0.3 | 0.4 | 2.1865 | 26582.1 | 1 | Cum | 58123
10 | M 30 grade concrete using 20 mm HBG metal
cluding cost,conveyance and labour etc.
complete for Conical side wall excluding cost of
|  | 3.1416 | 8.1 | 0.2 | 3.68 | 18.7289 | 32375.3 | 1 | Cum | 606354
11 | M 30 grade concrete using 20 mm HBG metal
including cost,conveyance and labour etc.complete
| for top | Ring beam | excluding cost steel
|  | 3.1416 | 11 | 0.3 | 0.4 | 4.1469 | 27495.5 | 1 | Cum | 114021
12 | M 30 grade concrete using 20 mm HBG metal
including cost,conveyance and labour etc.complete
| for inner | Shaft | excluding cost steel
|  | 3.1416 | 1.35 | 1.55 | 0.15 | 0.98607 | 38741.5 | 1 | Cum | 38202
| Flat portion | 3.1416 | 1.95 | 0.6 | 0.15 | 0.55135 | 76456.7 | 1 | Cum | 42154
13 | M 30 grade concrete using 20 mm HBG metal
including cost,conveyance and labour etc.complete
| for top Dome |  | excluding cost steel
|  | 6.2832 | 9.85 | 1.5 | 0.125 | 11.6043
| Deduct manhole | 2 | 0.6 | 0.6 | 0.125 | 0.09
| deduct phenial | 0.7854 | 0.6 | 0.6 | 0.125 | 0.035343
[6 empty] | 11.4789 | 45035.6 | 1 | Cum | 516960
14 | Accoproof Cement plastering with CM(1:3) 20 mm thick
etc., complete for inside tank
| Side wall | 3.1416 | 8.1 | 3.68 | 1 | 93.6446
| Top of BS | 6.2832 | 5.18 | 0.79 | 1 | 25.7121
[6 empty] | 119.3566 | 2436.2 | 10 | Sqm | 29078
15 | Painting with Snowcem paint 2 coats over a primary coat including cost
and conveyance of all materials and labour charges, etc., complete
| Outside shaft | 3.1416 | 5.9 | 30 | 1 | 556.0619
| Bottom ring beam | 3.1416 | 6.1 | 0.4 | 1 | 7.6655
| Side wall | 3.1416 | 8.5 |  | 3.68 | 98.269
| Top doome | 6.2832 | 9.85 | 1.5 | 1 | 92.8341
| Top ring beam | 3.1416 | 11.3 |  | 0.4 | 14.2
769.0305
Deductions
| Manhole | 2 | 0.6 | 0.6 | 1 | 0.72
| Phenial | 0.7854 | 0.6 | 0.6 | 1 | 0.28274
| Door | 1x2 | 0.9 |  | 1.8 | 3.24
[6 empty] | 764.7877 | 1202.7 | 10 | Sqm | 91981
16 | Landing Slab for Ladder
| 0-5 mts | 3mts Ht | 0 | 7.21 | 0.125 | 0 | 85072.8889 | 1 | Cum | 0 | 0
| 5-8 mts | 6mts Ht | 0 | 7.21 | 0.125 | 0 | 85493.133 | 1 | Cum | 0 | 0
| 8-11 mts | 9 Mt Ht | 0 | 7.21 | 0.125 | 0 | 85913.3771 | 1 | Cum | 0 | 0
| 11-14 mts | 12Mt Ht | 0 | 7.21 | 0.125 | 0 | 86333.6212 | 1 | Cum | 0 | 0
| 14-17mts | 15mt Ht | 0 | 7.21 | 0.125 | 0 | 86753.8653 | 1 | Cum | 0 | 0
| 17-20mts | 18mt Ht | 0 | 7.21 | 0.125 | 0 | 87174.1094 | 1 | Cum | 0 | 0
| 20-23mts | 21mt Ht | 0 | 7.21 | 0.125 | 0 | 87594.3535 | 1 | Cum | 0 | 0
| 23-26mts | 23mt Ht | 0 | 7.21 | 0.125 | 0 | 88014.5976 | 1 | Cum | 0 | 0
| 26-29mts | 27mt Ht | 0 | 7.21 | 0.125 | 0 | 88434.8417 | 1 | Cum | 0 | 0
16 | Provision towards cost of steel and fabrication
| complete |  |  |  |  | 38 | 60670.4 | 1 | MT | 2305475 |  |  | 191.0376 | 19.1038 | Dia | Rate
17 | Valve Chambers |  | 24878 | 12221 |  |  | 61977 | 1 |  | 61977 |  |  | 350 chambers 2 nos and 80-1 No |  | 0.9 | 13464 | 150
18 | CI specials, valves |  | with 13.615% Overheads | [6 empty] | 1593461.7365
19 | Vertical connections fixing including bolts nuts, rubber packing | [8 empty] | 64440
20 | Lightning arrester | [5 empty] | LS |  |  | 5000 |  |  |  |  | 1.05 | 15601 | 300
21 | Spiral Staircase | [8 empty] | 237721 |  |  |  |  | 1.2 | 17996
22 | Water level indicater | [5 empty] | LS |  |  | 2500
23 | Provision for Name Board | [5 empty] | LS |  |  | 5000
24 | Provision for ladder inside the shaft FL to Top Door | [5 empty] | LS |  |  | 5000
25 | Railing all around Top slab | [5 empty] | LS |  |  | 10000
26 | Lader inside the shaft | [5 empty] | LS |  |  | 15000
27 | MS Doors at Floor Level and LWL Level | [5 empty] | LS |  |  | 5000
28 | Phinaial & Fly proof ventilator | [5 empty] | LS |  |  | 5000
29 | Manhole cover with frames-2nos | [5 empty] | LS |  |  | 3364
30 | Unfoseen items | [8 empty] | 11609.2635
[8 empty] | Total |  | 9775000

## OHBR-Col
Input data |  | Coulmns No |  | 6
Staging | 25.25 | Brace No |  | 6
|  | Brace length |  | 3.53
|  | Coulmn size |  | 0.45 | 0.45 |  |  |  | Total Coulmn Ht | 24.425
Val Ch 0.90 | 12221 | Brace size |  | 0.55 | 0.4
Valv Ch1.05 | 16533 | Foundation below G.L |  | 2.5
Valv Ch1.20 | 24878 | Raft beam size/Dia |  | 0.5 | 0.55 | 6.9
25% added | no | Raft slab depth |  | 0.4
Inlet LPM | 2178 | Raft slab dia and width |  | 9.15 | 0
|  | G.L Coulmn ht |  | 2.6
Bottom slab | Dome | Next coulmn ht |  | 2.6 |  | R | H
Top slab | Dome | Bottom slab thickness/Dia |  | 0.125 | 7 | 6.125 | 0.989
Side wall | 3.15 | Rng girder height |  | 0.55 | 0.4
capacity | 90000 | Side wall Ht& Thick&Dia |  | 3 | 0.1 | 7
Outlet LPM | 2178 | Topslab thick & dia |  | 0.075 | 7 | 6.075 | 1.13
G.L | 0 | Top slab ring girder wd/ht |  | 0.2 | 0.15
|  | Tank Capacity |  | 90000 | OHBR | Staging | 25.25
CPWS SCHEME TO DISTRICT
|  | M.W.L | 28.1 |  | Free board | 0.15
|  | L.W.L | 25.25 |  | Dead storge | 0.15
|  | G.L | 0
|  | Inlet pipe | Outlet pipe | Scour pipe | Over flow
| Rec.dia | 300 | 300 | 80 | 300
| 2 Mt pipe | 14 | 12 | 12 | 14
| 0.90 Mt pipe | 0 | 1 | 1 | 0
| 0.60 Mt pip | 1.1 | 1.25 | 1.1 | 1.1
| Duck foot bend | 1 | 1 | 1 | 1
| Bell mouth | 1 | 1 | 1 | 1
| Sluice valve | 1 | 1 | 1 | 0
|  | 52 | 639.26 | 33241.52
|  | 17 | 139.21 | 2366.57
40593
Total
| CI Sp.Cost | 271863.5282 | 246472.3305 | 47052.1436 | 271863.5282 | 837252
| Slucivalve Cost | 67740 | 67740 | 11025 | 0 | 146505
CPWS SCHEME TO DISTRICT
Detailed estimate cum abstract estimate
Name of the work:Contruction of |  |  | 90000 | Lts capacity | OHBR | staging | 25.25 | Mts
Wind speed=200 KMPH | [5 empty] | Est.Cost Rs | 56.5 | Lakhs
S.no | Description |  |  |  |  | Quantity | Rate | Amount
1 | Earth work excavation in all type of soils with intial lead and lift etc complete
|  | 1xp/4 | 10.35 | 10.35 | 3 | 252.503 | 158.8 | 40097
|  | 1xp/4 | 3.8 | 3.8 | 0.65 | 7.3747 | 204.2 | 1506
2 | CC(1:4:8)using 40 mm HBG metal icluding Cost and conveyance of the all materials etc complete.
|  | 1xp/4 | 10.35 | 10.35 | 0.3 | 25.2503 | 4470.5 | 112881
3 | Filling the Foundation with sand including cost,conveyance ,watering and ramming etc complete.
|  | 1xp/4 | 10.35 | 10.35 | 0.3 | 25.2503 | 937.7 | 23677
4 | M 30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for bottom raft
|  | 1xp/4 | 1 | 1
|  | 1xp/4 | 9.15 | 9.15 | 0.4 | 26.3128 | 9199.4 | 242062
5 | M 30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Ring beam
|  | p | 6.9 | 0.5 | 0.15 | 1.6264 | 15613.3 | 25394
6 | M 30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Column
| Below G.L | 6 | 0.45 | 0.45 | 1.8 | 2.19
| 0 - 3 Mts | 6 | 0.45 | 0.45 | 2.45 | 2.98
[6 empty] | 5.17 | 23528.1969 | 121641
| 3 - 4 Mts | 6 | 0.45 | 0.45 | 1 | 1.22 | 23681.3532 | 28891
| 4 - 5 Mts | 6 | 0.45 | 0.45 | 1 | 1.22 | 23834.5095 | 29078
| 5 - 6 Mts | 6 | 0.45 | 0.45 | 0.45 | 0.55 | 23987.6658 | 13193
| 6-7 Mts | 6 | 0.45 | 0.45 | 1 | 1.22 | 24140.8221 | 29452
| 7-8 Mts | 6 | 0.45 | 0.45 | 1 | 1.22 | 24293.9784 | 29639
| 8-9 Mts | 6 | 0.45 | 0.45 | 0.45 | 0.55 | 24447.1347 | 13446
| 9-10 Mts | 6 | 0.45 | 0.45 | 1 | 1.22 | 24600.291 | 30012
| 10-11 Mts | 6 | 0.45 | 0.45 | 1 | 1.22 | 24753.4473 | 30199
| 11-12 Mts | 6 | 0.45 | 0.45 | 0.45 | 0.55 | 24906.6036 | 13699
| 12-13mts | 6 | 0.45 | 0.45 | 1 | 1.22 | 25059.7599 | 30573
| 13-14mts | 6 | 0.45 | 0.45 | 1 | 1.22 | 25212.9162 | 30760
| 14-15mts | 6 | 0.45 | 0.45 | 0.45 | 0.55 | 25366.0725 | 13951
| 15-16mts | 6 | 0.45 | 0.45 | 1 | 1.22 | 25519.2288 | 31133
| 16-17mts | 6 | 0.45 | 0.45 | 1 | 1.22 | 25672.3851 | 31320
| 17-18mts | 6 | 0.45 | 0.45 | 0.45 | 0.55 | 25825.5414 | 14204
| 18-19mts | 6 | 0.45 | 0.45 | 1 | 1.22 | 25978.6977 | 31694
| 19-20mts | 6 | 0.45 | 0.45 | 1 | 1.22 | 26131.854 | 31881
| 20-21mts | 6 | 0.45 | 0.45 | 0.45 | 0.55 | 26285.0103 | 14457
| 21-22mts | 6 | 0.45 | 0.45 | 1 | 1.22 | 26438.1666 | 32255
| 22-23mts | 6 | 0.45 | 0.45 | 1 | 1.22 | 26591.323 | 32441
| 23-24mts | 6 | 0.45 | 0.45 | 0.875 | 1.06 | 26744.4793 | 28349
7 | M 30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Braces
| 2 | 6 | 0.55 | 0.4 | 3.53 | 9.3192 | 20061.8903 | 186961
5- 8 Mts
| 1 | 6 | 0.55 | 0.4 | 3.53 | 4.6596 | 20521.3592 | 95621
8- 11 Mts
| 1 | 6 | 0.55 | 0.4 | 3.53 | 4.6596 | 20980.8281 | 97762
| 11- 14 Mts | [8 empty] | 3.0769
| 1 | 6 | 0.55 | 0.4 | 3.53 | 4.6596 | 21440.297 | 99903
14- 17 mts
| 1 | 6 | 0.55 | 0.4 | 3.53 | 4.6596 | 21899.7659 | 102044
17- 20 Mts
| 1 | 6 | 0.55 | 0.4 | 3.53 | 4.6596 | 22359.2348 | 104185
20-23 Mts
| 1 | 6 | 0.55 | 0.4 | 3.53 | 4.6596 | 22818.7038 | 106326
9 | M 30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Ring Girder
|  | p | 9.15 | 0.4 | 0.55 | 6.3266 | 22692.8 | 143568
| Top Girder | p | 7.2 | 0.2 | 0.15 | 0.67886 | 44189.5 | 29998
10 | M 30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Bottom Doome
|  | 2p | 6.125 | 0.989 | 0.125 | 4.7576 | 35514.7 | 168966
11 | M 30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Side Walls
|  | p | 7.1 | 0.1 | 3 | 6.6943
| Haunches | p 1/2 | 6.85 | 0.15 | 0.15 | 0.2422
[6 empty] | 6.9365 | 49679 | 344597
12 | M 30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Top Doome
|  | 2p | 6.075 | 1.13 | 0.075 | 3.2349 | 52150.2 | 168703
13 | M 30 grade concrete using 20 mm HBG metal including cost and conveyance of all the materials,but excluding the cost of the steel etc complete for Top Cantilever
|  | p | 8.1 | 0.9 | 0.15 | 3.4367 | 83487.1 | 286921
14 | Accoproof plastering with CM(1:3),20mm thick including cost and conveyance of all the materials ect complete.
| Top Doome |  | 2p | 6.075 | 1.13 | 43.1325
| Side wall inside |  | p | 7 | 3 | 66
| Bottom Doome |  | 2p | 6.125 | 0.989 | 38.0612
[5 empty] | Toatl | 147.1937 | 2436.2 | 35859
15 | Cement plastering with CM(1:3),12mm thick including cost and conveyance of all the materials ect complete.
| Side walls out side |  | p | 7.2 | 3 | 67.89
| Ring girder |  | p | 6.9 | 1.35 | 29.28
| Coulmns |  | 6 | 1.8 | 8.35 | 90.18
| Braces | 7 | 6 | 1.9 | 3.53 | 281.69
| Cantilever |  | p | 8.1 | 1.95 | 49.64
| Topring beam |  | p | 7.2 | 0.45 | 10.18
[5 empty] | Toatl | 528.86 | 1491.9 | 78901
16 | Snowcem painting including cost and conveyance of all the materials ect complete.
[6 empty] | 528.86 | 1202.7 | 63606
17 | Supply and placing of the HYSD bars, fabrication including cost and conveyance of all the materials etc complete.
[6 empty] | 15.4436 | 60670.4 | 936968
| Valve Chambers |  |  |  |  | 3 |  | 61977
| Lightning arrester | [6 empty] | 5000
| RCC ladder in side the tank 2 Nos | [6 empty] | 7000
| CI specials fixing charges | [6 empty] | 40593
| Water level indicater | [6 empty] | 2500
| Painting of name board | [6 empty] | 2000
| Spiral Staircase | [6 empty] | 237721
| painting to hand railing | [6 empty] | 2000
| Phinaial & Mosquito proof ventilator | [6 empty] | 1000
| Manhole cover |  | 2 Nos |  |  |  |  | 3364
| CI conections | [6 empty] | 837252
| CI Sluice valves | [6 empty] | 146505
| Add Overheads & C.P on CI Specials & Valves |  |  |  | 13.61% |  |  | 133939
| Unforcen item | [6 empty] | 10375
[7 empty] | Total | 5650000
5639625
[11 empty] | Dia | Rate
[11 empty] | 0.9 | 12221 | 150
[11 empty] | 1.05 | 16533 | 300
[11 empty] | 1.2 | 24878
|  | Rate per Lt = |  | 61.1743
Note:- SBC taken as 10 T/ sqmt

## OHSR Lit
Input data
|  |  |  | OHSR | yes
|  |  |  | OHSR Capacity | 60000
|  |  |  | Staging | 9.6 | 12.90,9.75
|  |  |  | Valv Ch 0.90 | 12221
|  |  |  | Vlav Ch1.05 | 16533
|  |  |  | Valv Ch1.20 | 24878 |  | B
|  |  |  | Valves 50% add | no |  | FALSE
|  |  |  | Basic rate | 29.76 |  | OHSR
|  |  |  | Cement rate | 6400 |  | Inlet | 200
|  |  |  | Steel rate | 42000 |  | Oulet | 200
|  |  |  | PH SSR Cem rate | 6400 |  | Over flow | 200
|  |  |  | PH SSR steel rate | 42000
| 60000 | Lts Capacity OHSR
CPWS SCHEME TO DISTRICT
| M.W.L | 11.8 |  | Free board | 0.15
| L.W.L | 9.6 |  | Dead storge | 0.15
| G.L | 0
| Inlet pipe | Outlet pipe | Scour pipe | Over flow
Rec.dia | 80 | 100 | 80 | 80
2 Mt pipe | 5 | 4 | 4 | 5
0.90 Mt pipe | 1 | 1 | 1 | 1
0.60 Mt pip | 1.8 | 1.6 | 1.45 | 1.8
Duck foot bend | 1 | 1 | 1 | 1
Tail Piece | 1 | 0 | 0 | 1
Bell mouth | 1 | 0 | 1 | 1
90o D/f bend | 1 | 0 | 0 | 1
Sluice valve | 1 | 1 | 1 | 0
Semicircular Bend | 0 | 0 | 1 | 0
upto 350mm dia DI Wafer Butterfly valves and
above 350mm dia DI D/F Butterfly valves
Total
CI Sp.Cost | 25905.8488 | 24459.8508 | 21680.7712 | 25905.8488 | 97952
Butterfly valves Cost DI | 9019.5 | 11897.55 | 9019.5 | 0 | 29937
Wind Velocity | 150 | KMPH |  | Velocity | 41.67 | Pressure | 104.18
Construction of | 60000 | Lts capacity OHSR with |  | 9.6 | Mts staging
CPWS SCHEME TO DISTRICT
[6 empty] | Est.Cost Rs | 1980000
Construction of 60000 Lts Capacity OHSR with 9.6 m staging with raft foundation
plastering with CM(1:3) 2 coats of Weather proof emulsion painting for external surfaces, and 3 coats of epoxy paint to inner surface of the reservoir including roof dome, lettering as per Dept Direction, S/Fof the CI D/F Pipes verticals, vlaves, Execution as per Design and drawigns supplied by the Dept., including the cost and conveyance of the all materials , Bends , Specials Etc complete including the following.- M30 Grade Concrete
b)D.I man hole covers with frame of size 0.60 X 0.60 mts -2 Nos (light duty)
c) DI Swan Neck ventilators shall be provided in Top dome/slab with flyproof mesh
d)RCC Phinial with copper or Stainless stell flyproof mesh
e)RCC or Aluminium ladder inside of 0.60 mts width
f)RCC spiral stair case with handrailing upto 200kl
for above 200kl capacity Doglegged staircase with flight width of 1mt and landing of 1.2mts and SS Handrailing upto 1mt Thedogleggedstaircaseshallbeenclosedwithbrick/CRSwallonthreesidesandfrontsidewithM.Scollapsiblegateupto1stbracelevel from ground level to prevent unauthorized entry.
g)Waterlevel indicator of good quality with ebonite/copper float approved pattern - 1 No.
h)Lightening arrestor of approved pattern 1 No complete including conductor earthing
J) Railling with Stainless Steel of grade 304 in two rows around OHSR fixed in RCC (1:2:4) of post of size 100x75x75mm with 1.5m m itervals around the pheriphary on top of OHSR
A) Basic cost | 60000 | X | 29.76 |  |  | : Rs | 1785600
B) | (With out Rural area allowence Due to MA) | [5 empty] | 0
C) Add for increse in price of cement
| 6400 | 6400 | 0.7 | 1785600 |  | : Rs | 0
( 100 X 100)
D) Add for increase/ Decrease in price of Steel
| 42000 | 42000 | 2 | 1785600 |  | : Rs | 0
( 1000 X 100)
E) Deduct for staging below 10 Mts by .05 Paise per Lt | [5 empty] | : Rs | 1200
F) Add or deduct for Wind Pressure
| 104.18 | 350 | 5 | 1785600 |  | : Rs | -219468
| ( 100 X 100) | [9 empty] | 12221
G) Cost of CI Specials | [5 empty] | : Rs | 97952 |  |  |  | 16533
45287
H) Cost of D.I Butter fly valves |  |  |  | 3 Nos |  | : Rs | 29937
I) Cost of valve chambers |  |  |  | 3 Nos |  | : Rs | 45287 |  |  |  |  | 1695221 | Don’t delete
1 No | 12221 | 2 Nos | 16533 |  |  | Total | 1740508 |  |  |  |  | For valve chambers refer valves VC 80 etc
J) Add Overheads and C.P |  |  |  | 13.61% |  |  | 230804
K) Provision for unforceen items | [5 empty] | : Rs | 8688
|  |  |  | Total cost |  |  | 1980000 |  |  | 1971312 |  |  |  | Dia | Valve Ch rate
[14 empty] | 0.9 | 12221 | 150
|  | Rate per lt | 32.8552 | [10 empty] | 1.05 | 16533 | 300
[14 empty] | 1.2 | 24878
60
80

## VC 80
Sub-estimate
Construction of 0.90mx0.75mx1.05m Size valve chamber
for Pipes of Dia Upto 80mm dia
Sno | Description | No | L | B | D | Qty | Unit | Rate | Per | Amount
1 | Earth work excavation and depositing on bank with an initial lead of 50m and lift of 3.0m in all types of soils except hard rock requiring blasting for founadtion | 1x1 | 1.3 | 1.15 | 1.35 | 2.0183 | Cum | 158.8 | cum | 320
2 | CC(1:4:8) Using 40mm HBG metal including cost and conveyance of all materials,labour charges etc., complete for foundation. | 1x1 | 1.3 | 1.15 | 0.15 | 0.22425 | Cum | 4503.5 | Cum | 1010
3 | RCC(1:1.5:3) using 20mm HBG metal including cost and conveyance of all materilas,labour charges and centering etc., complete but excluding cost of steel and its fabrication.
| a) For Bottom raft | 1x1 | 1.3 | 1.15 | 0.1 | 0.1495 | Cum | 7284.3 | Cum | 1089
| b) For Side walls allround | 1x1 | 3.7 | 0.1 | 1.05 | 0.3885 | Cum | 18586.9 | Cum | 7221
| c) For Pre cast top slab(100mm thick) | 1x1 | 1.1 | 0.95 | 0.1 | 0.1045 | Cum | 7284.3 | Cum | 761
4 | Cost and supply of Steel including fabrication charges |  |  |  |  | 30 | Kg | 60670.4 | MT | 1820
5 | For Isolated works 50% extra | [8 empty] | 6111
| Total Amount per Each Chamber | [8 empty] | 18332
[11 empty] | 12221 | for OHSRs, OHBRs

## VC 200
Sub-estimate
Construction of 0.9mx0.90mx1.40m Size RCC Valve Chambers
for Pipe lines of Dia Up more than 80mm and upto 200mm
SL No. | Description | No | L | B | D | Qty | Unit | Rate | Per | Amount
1 | Earth work excavation and depositing on bank with an initial lead of 10m and lift of 2.0m in all types of soils except hard rock requiring blasting for founadtion | 1x1 | 1.3 | 1.3 | 1.65 | 2.7885 | Cum | 158.8 | Cum | 443
2 | CC(1:4:8) Using 40mm HBG metal including cost and conveyance of all materials,labour charges etc., complete for foundation. | 1x1 | 1.3 | 1.3 | 0.15 | 0.2535 | Cum | 4503.5 | Cum | 1142
3 | RCC(1:1.5:3) using 20mm HBG metal including cost and conveyance of all materilas,labour charges and centering etc., complete but excluding cost of steel and its fabrication.
| a) For Bottom raft | 1x1 | 1.3 | 1.3 | 0.1 | 0.169 | Cum | 7284.3 | Cum | 1231
| b) For Side walls allround | 1x1 | 4 | 0.1 | 1.4 | 0.56 | Cum | 18586.9 | Cum | 10409
| c) For Pre cast top slab(100mm thick) | 1x1 | 1.1 | 1.1 | 0.1 | 0.121 | Cum | 7284.3 | Cum | 881
4 | Cost and supply of Steel including fabrication charges |  |  |  |  | 40 | Kg | 60670.4 | MT | 2427
5 | For Isolated works 50% extra | [8 empty] | 8267
| Total Amount per Each Chamber | [8 empty] | 24800
16533

## VC 450
Sub-estimate
Construction of 1.05mx1.20mx1.70m Size RCC Valve Chambers
of Pipe line dia above 200mm and upto 400mm
SL No. | Description | No | L | B | D | Qty | Unit | Rate | Per | Amount
1 | Earth work excavation and depositing on bank with an initial lead of 10m and lift of 2.0m in all types of soils except hard rock requiring blasting for founadtion | 1x1 | 1.65 | 1.8 | 1.95 | 5.79 | Cum | 158.8 | Cum | 919
2 | CC(1:4:8) Using 40mm HBG metal including cost and conveyance of all materials,labour charges etc., complete for foundation. | 1x1 | 1.65 | 1.8 | 0.15 | 0.45 | Cum | 4503.5 | Cum | 2027
3 | RCC(1:1.5:3) using 20mm HBG metal including cost and conveyance of all materilas,labour charges and centering etc., complete but excluding cost of steel and its fabrication.
| a) For Bottom raft | 1x1 | 1.45 | 1.6 | 0.1 | 0.23 | Cum | 7284.3 | Cum | 1675
| b) For Side walls allround | 1x1 | 4.9 | 0.1 | 1.7 | 0.83 | Cum | 18586.9 | Cum | 15427
| c) For Pre cast top slab(100mm thick) | 1x1 | 1.25 | 1.4 | 0.1 | 0.18 | Cum | 7284.3 | Cum | 1311
4 | Cost and supply of Steel |  |  |  |  | 58 | Kg | 60670.4 | MT | 3519
5 | For Isolated works 50% extra | [8 empty] | 12439
| Total Amount per Each Chamber | [8 empty] | 37317
24878

## VC 600
Sub-estimate
Construction of 1.20mx1.20mx2.10m Size RCC Valve Chambers
of Pipe line Dia above 400mm and upto 500mm
Sno | Description | No | L | B | D | Qty | Unit | Rate | Per | Amount
1 | Earth work excavation and depositing on bank with an initial lead of 10m and lift of 2.0m in all types of soils except hard rock requiring blasting for founadtion | 1x1 | 1.8 | 1.8 | 2.35 | 7.61 | Cum | 158.8 | Cum | 1208
2 | CC(1:4:8) Using 40mm HBG metal including cost and conveyance of all materials,labour charges etc., complete for foundation. | 1x1 | 1.8 | 1.8 | 0.15 | 0.49 | Cum | 4503.5 | Cum | 2207
3 | RCC(1:1.5:3) using 20mm HBG metal including cost and conveyance of all materilas,labour charges and centering etc., complete but excluding cost of steel and its fabrication.
| a) For Bottom raft | 1x1 | 1.6 | 1.6 | 0.1 | 0.26 | Cum | 7284.3 | Cum | 1894
| b) For Side walls allround | 1x1 | 5.2 | 0.1 | 2.1 | 1.09 | Cum | 18586.9 | Cum | 20260
| c) For Pre cast top slab(100mm thick) | 1x1 | 1.4 | 1.4 | 0.1 | 0.2 | Cum | 7284.3 | Cum | 1457
4 | Cost and supply of Steel |  |  |  |  | 74 | Kg | 60670.4 | MT | 4490
5 | For Isolated works 50% extra | [8 empty] | 31516
| Total Amount per Each Chamber incl.VAT at 4% | [8 empty] | 63032 | 31516

## VC 700
Sub-estimate
Construction of RCC valve Chamber of Size (1.70mx1.20mx2.10m)
of Pipe line Dia above 500mm and upto 700mm
SL No | Description of Item | No | Length | Width | Depth | Qty | Unit | Rate | Per | Amount Rs.
1 | Earth work Excavation in Ordinary,Hard gravelly and disintegrated rock for a lead of 10m and lift of 2m for chamber | 1x1 | 2.5 | 1.8 | 2.35 | 10.575 | Cum | 158.8 | cum | 1679
2 | PCC (1:4:8) using 40mm HG metal including cost and conveyance of all materials and labour charges etc complete for leveling course ov chamber bottom | 1x1 | 2.5 | 1.8 | 0.15 | 0.675 | Cum | 4503.5 | 1Cum | 3040
3 | RCC(1:1.5:3) nominal mix using 20mm HBG metal including cost and conveyance of all materials and labour charges etc., complete for Bottm slab of Chamber | 1x1 | 2.3 | 1.8 | 0.15 | 0.621 | Cum | 7284.3 | 1Cum | 4524
4 | RCC(1:1.5:3) nominal mix using 20mm HBG metal including cost and conveyance of all materials and labour charges etc., complete for side wall of Chamber
|  | 1x2 | 2.1 | 2 | 0.2 | 1.68
|  | 1x2 | 1.2 | 2 | 0.2 | 0.96
[6 empty] | 2.64 | Cum | 13361.8 | 1Cum | 35275
5 | RCC(1:1.5:3) nominal mix using 20mm HBG metal including cost and conveyance of all materials and labour charges etc., complete for pre cast top slab of Chamber | 1x1 | 2.1 | 1.6 | 0.1 | 0.336 | Cum | 7284.3 | 1Cum | 2448
6 | Suply and fabrication of charges steel |  |  |  |  | 190 | Kgs | 60670.4 | MT | 11527
8 | Extra for Isolation of Work at 50% | [8 empty] | 29247
| Total Rs. | [8 empty] | 87740 | 58493

## VC 1000
Sub-estimate
Const. of RCC valve Chamber of Size (3.00mx2.00mx2.50m)
above 700mm up to 1000mm dia pipe line
Sno | Description of Item | No |  |  | Length | Width | Depth | Qty | Unit | Rate | Per | Amount Rs.
1 | Earth work Excavation in Ordinary,Hard gravelly and disintegrated rock for a lead of 10m and lift of 2m for chamber | 1 | x | 1 | 3.8 | 2.8 | 2.75 | 29.26 | Cum | 158.8 | cum | 4646
2 | PCC (1:4:8) using 40mm HG metal including cost and conveyance of all materials and labour charges etc complete for leveling course ov chamber bottom | 1 | x | 1 | 3.8 | 2.8 | 0.15 | 1.596 | Cum | 4503.5 | Cum | 7188
3 | RCC(1:2:4) nominal mix using 20mm HBG metal including cost and conveyance of all materials and labour charges etc., complete
a) | for Bottm slab of Chamber | 1 | x | 1 | 3.6 | 2.6 | 0.15 | 1.404 | Cum | 7284.3 | Cum | 10227
b) | for side wall of Chamber | 1 | x | 2 | 3.4 | 0.2 | 2.5 | 3.4
|  | 1 | x | 2 | 2 | 0.2 | 2.5 | 2
[8 empty] | 5.4 | Cum | 13361.8 | Cum | 72154
c) | pre cast top slab of Chamber | 1 | x | 1 | 3.4 | 2.4 | 0.15 | 1.224 | Cum | 7284.3 | cum | 8916
4 | Supply and fabrication charges of steel | [6 empty] | 387 | Kgs | 60670.4 | MT | 23479
5 | Extra for Isolation of Work at 50% | [10 empty] | 63305
| Total Rs. | [10 empty] | 189915 | 126610